CONTENTS

1	Main menu	4

2	Structure	5

2.1	System	5

2.1.1	Objects	6

2.1.1.1	Creating new object	6

2.1.1.2	Removal of the object	6

2.1.2	Partitions	7

2.1.2.1	Creating new partition	9

2.1.2.2	Removal of the partition	9

2.1.2.3	Adding zone to partition	9

2.1.2.4	Removal of the zone from the partition	9

2.1.2.5	Timer of partition	10

2.1.3	Partitions settings printout	10

2.2	Hardware	10

2.2.1	Mainboard	11

2.2.2	Keypad bus	11

2.2.2.1	INT-KLCD	12

2.2.2.1.1	Volume/filter	16

2.2.2.1.2	State inspections	16

2.2.2.1.3	User functions definition	16

2.2.2.2	INT-KLCDR	17

2.2.2.2.1	Volume/filter	20

2.2.2.2.2	State inspections	20

2.2.2.2.3	User functions definition	20

2.2.2.2.4	Proximity cards	21

2.2.2.3	INT-KSG	21

2.2.2.3.1	Volume/filter	24

2.2.2.3.2	State inspections	24

2.2.2.3.3	User functions definition	25

2.2.2.3.4	Macro Commands	25

2.2.2.3.5	Defining the macro commands	27

2.2.2.3.6	Status screen	28

2.2.2.4	INT-KWRL	29

2.2.2.4.1	Volume/filter	32

2.2.2.4.2	State inspections	32

2.2.2.4.3	User functions definition	33

2.2.2.4.4	Proximity cards	33

2.2.2.5	INT-TSG	33

2.2.2.5.1	State inspections	37

2.2.2.5.2	User functions definition	38

2.2.2.5.3	Macro Commands	38

2.2.2.5.4	Defining the macro commands	41

2.2.2.5.5	Status screen	42

2.2.2.6	INT-TSH	43

2.2.2.6.1	State inspections	46

2.2.2.6.2	User functions definition	47

2.2.2.6.3	Macro Commands	47

2.2.2.6.4	Defining the macro commands	50

2.2.2.6.5	Status screen	51

2.2.2.7	INT-TSI	53

2.2.2.7.1	State inspections	56

2.2.2.7.2	User functions definition	56

2.2.2.8	ETHM-1	56

2.2.2.8.1	IP filter	60

2.2.2.8.2	User functions definition	60

2.2.2.9	INT-GSM	60

2.2.2.9.1	INT-GSM functions	62

2.2.2.9.2	GSM phone	62

2.2.2.9.3	Pre-paid support	64

2.2.2.9.4	SMS messaging / CLIP control	65

2.2.2.9.5	SMS control	66

2.2.2.9.6	Reporting	68

2.2.2.9.7	Remote firmware update	69

2.2.2.9.8	User functions definition	70

2.2.2.10	ETHM+GSM	70

2.2.2.10.1	INT-GSM functions	73

2.2.2.10.2	GSM phone	73

2.2.2.10.3	Pre-paid support	75

2.2.2.10.4	SMS messaging / CLIP control	76

2.2.2.10.5	SMS control	77

2.2.2.10.6	Reporting	79

2.2.2.10.7	Remote firmware update	80

2.2.2.10.8	IP filter	81

2.2.2.10.9	User functions definition	81

2.2.2.11	CA-64 PTSA	81

2.2.2.12	INT-RS	82

2.2.2.13	GUARDX on RS-232	82

2.2.2.13.1	State inspections	84

2.2.2.14	GUARDX/INTEGRA CONTROL	84

2.2.2.14.1	State inspections	86

2.2.2.14.2	Macro Commands	87

2.2.2.14.3	Defining the macro commands	90

2.2.2.15	DLOADX (RS-232)	90

2.2.2.15.1	State inspections	92

2.2.2.16	DLOADX (modem)	93

2.2.2.16.1	State inspections	94

2.2.2.17	Copy	95

2.2.3	Expansion modules bus	95

2.2.3.1	INT-CR/IT	96

2.2.3.2	INT-S	97

2.2.3.3	INT-SCR	100

2.2.3.4	INT-ENT	103

2.2.3.5	INT-SZ	104

2.2.3.6	CA-64 SR	106

2.2.3.7	CA-64 DR	108

2.2.3.8	INT-RX	110

2.2.3.9	CA-64 E	110

2.2.3.10	CA-64 Ei / INT-E	110

2.2.3.11	CA-64 EPS	111

2.2.3.12	CA-64 EPSi / INT-EPS	112

2.2.3.13	INT-ADR	113

2.2.3.14	CA-64 ADR / INT-ADRPS	113

2.2.3.15	CA-64 O / INT-O	114

2.2.3.16	CA-64 OPS / INT-OPS	114

2.2.3.17	INT-ORS	114

2.2.3.18	INT-ORSPS	115

2.2.3.19	INT-IORS	115

2.2.3.20	INT-IORSPS	116

2.2.3.21	INT-PP	118

2.2.3.22	INT-PPPS	119

2.2.3.23	ACU-100	120

2.2.3.23.1	Zones/Outputs	121

2.2.3.23.2	INT-KWRL	122

2.2.3.23.3	Adding wireless device	123

2.2.3.23.4	Removing wireless device	124

2.2.3.23.5	Configuring the ABAX wireless devices	124

2.2.3.23.6	Adding wireless keypad	126

2.2.3.23.7	Removing wireless keypad	126

2.2.3.24	INT-VG	126

2.2.3.25	CA-64 SM	127

2.2.3.26	INT-KNX	127

2.2.3.27	INT-KNX-2	129

2.2.3.28	INT-AV	131

2.2.3.29	Users of module	132

2.2.3.30	Exp. modules order	132

2.2.4	Add module	132

2.2.5	Identification	133

3	Options	133

3.1	Telephone	133

3.2	Printer	135

3.3	Times	136

3.4	Other	137

3.5	Arming	139

3.6	Service	140

3.7	User’s default authority level	140

4	Zones	140

4.1	Zone types	145

4.2	Counters	148

4.3	Bypasses	148

4.4	Arm/Disarm groups	149

5	Outputs	149

5.1	Output functions	152

5.2	Logical functions of outputs	156

5.3	Output groups	157

6	Timers	157

6.1	User schedules	158

6.2	Timers settings printout	158

7	Reporting	159

7.1	Monitoring stations	159

7.1.1	Reporting options	162

7.2	SIA-IP	162

7.3	Identifiers assignment	163

7.4	Event codes	163

7.5	Starting the reporting	164

7.5.1	Telephone reporting	164

7.5.2	Ethernet reporting	165

7.5.3	GPRS reporting	165

7.5.4	SMS reporting	166

8	Messaging	167

8.1	Telephone numbers	167

8.2	Events assignment	168

8.3	Clearing	168

8.4	Pager messages	169

8.4.1	Pager types	169

8.5	Voice messages	169

8.6	SMS messaging	169

8.7	Starting the voice messaging	170

9	E-mail messaging	170

9.1	Mail server	171

10	Answering and remote control	171

10.1	Activation of the phone calls answering	172

10.2	Activation of the remote control	172

11	Service note	172

12	Users	173

12.1	User types	176

12.2	Adding administrator	177

12.3	Adding user	177

12.4	Removing administrator/user	177

12.5	Adding proximity card	178

12.6	Removing proximity card	178

12.7	Adding DALLAS iButton	178

12.8	Removing DALLAS iButton	179

13	Keyfobs INT-RX	179

13.1	Adding 433 MHz keyfob	180

13.2	Removing 433 MHz keyfob	180

14	Keyfobs ABAX	181

14.1	Adding ABAX keyfob	182

14.2	Removing ABAX keyfob	183

15	Data comparison	183

16	Event log	183

16.1	Choose	184

16.2	Print	185

16.3	Grade2 events	185

17	System state	186

17.1	Keypad	186

17.2	Partitions state	186

17.3	Zones state	186

17.4	Outputs, timers, tampers, doors	186

17.5	Troubles	187

17.6	Module power supply	187

17.7	Wireless devices	187

17.7.1	Wireless system	188

18	Configuration	189

18.1	Port RS-232	189

18.2	Modem	189

18.2.1	Configuring the modem connected to computer	190

18.3	Data	191

19	Connection	191

19.1	Port COM	191

19.2	Modem 300bps	193

19.3	Modem - INTEGRA with ext. modem	194

19.4	Modem ISDN/GSM	196

19.5	TCP/IP: DLOADX -> ETHM	199

19.6	TCP/IP: DLOADX <- GSM/GPRS	200

19.7	TCP/IP: DLOADX <- ETHM/INT-GSM	201

19.8	TCP/IP: SATEL server	204

19.9	Connecting the external modem to the control panel	206

19.9.1	Configuring the modem to be connected to control panel	208

19.10	Connecting the RS-232 ports of control panel and ETHM-1 Plus / ETHM-1 / INT-GSM module	208

19.11	Communication identifiers and establishing connection	209

20	Communication	209

20.1	Communication options	209

20.1.1	Data comparison: Write	210

20.2	Connection settings	210

21	Programming telephone numbers	212

# Main menu

1 - type of alarm control panel.

2 - name of alarm system / data file.

3 - information on data writing/reading progress.

4 - information on the way of communication with the alarm control panel:

COMn [n - number of computer COM port] - via the RS-232 port,

Modem - via the modem,

TCP/IP - via the Ethernet/GPRS.

###### Buttons

- click to open the Structure window.

- click to open the Options window.

- click to open the Zones window.

- click to open the Outputs window.

- click to open the Timers window.

- click to open the Reporting window.

- click to open the Messaging window.

- click to open the E-mail messaging window.

- click to open the Answering and remote control window.

- click to open the Service note window.

- click to open the Users window.

- click to open the window with information on errors made when configuring the alarm system.

- click to open the Data comparison window.

- click to synchronize program data and control panel data (read/write data).

- click to write data to the control panel.

- click to open the event log window.

- click to terminate data reading/writing.

- click to write computer clock time to the control panel.

- click to write data into the control panel FLASH memory.

- click to display virtual keypad (see: Keypad).

- click to display the drop-down menu, in which the system supervisory tools are available (see: System state).

- click to open the Configuration window. The Configuration window will not open, when the DLOADX program is connected to the control panel via modem or Ethernet/GPRS. Instead, a window with the connection information will open. Opening the Configuration window will only be possible after the connection is ended.

- click to display the drop-down menu, where you can select the way of communication with the alarm control panel (see: Connection).

- click to:

- enable/disable the COM port,

- open the connection information window (remote programming).

Color of the button icon has the following meanings:

green - connection OK,

alternating green and yellow - data transfer going on,

red - no communication with the control panel,

gray - COM port disabled.

# Structure

System

Hardware

## System

The INTEGRA Plus alarm control panels enable a two-level division of the alarm system:

- the control panel zones are grouped into partitions,

- a group of partitions constitutes an object (subsystem).

The system structure (objects, partitions and zones) is presented in tree form. After you click on any of the tree elements, you can start configuring it.

###### Buttons

Add - click to add a new system element (object / partition / zone).

Delete - click to remove the highlighted system element.

Print - click to open the Partitions settings printout window.

Objects

Partitions

Zones

### Objects

By default, one object is created in the control panel. You can create up to 8 objects. The objects are treated as separate alarm systems. It is possible to configure the control panel so that the objects can have separate controls (keypads) and own sirens or, alternatively, can have common hardware.

In case of the common keypads, the controlled object is recognized based on the code of the user giving the command.

Events from each object are sent to the central monitoring station with individual identifiers (Monitoring stations). When the Contact ID or SIA format is selected, the control panel distributes events automatically. In case of other formats, you have to assign events to identifiers (Identifiers assignment).

-----------------------------------------------------------

Object name - individual name of the object (up to 16 characters).

Notes - additional information related to the objects.

Creating new object

Removal of the object

#### Creating new object

- In the Structure window, System tab, click on the branch with system name

- Click on the Add button. A new object will be created.

- Click on the , to write the changes to the control panel.

#### Removal of the object

Note: The object 1 cannot be removed.

- In the Structure window, System tab, click on the branch with the name of object you want to remove.

- Click on the Delete button. The Confirm window will open.

- Click on the Yes button. The Confirm window will close and the object will be removed.

- Click on the , to write the changes to the control panel.

### Partitions

The partition is a separated area within the premises protected by the security alarm system. The subdivision into partitions enables arming/disarming the system only in part of the protected area, as well as limiting access to some portion of the premises to selected users.

-----------------------------------------------------------

Partition name - individual name of partition (up to 16 characters).

Belongs to object - the object the partition belongs to.

###### Partition type

Armed with code - the partition can be armed/disarmed by the user.

With temporary blocking - the partition can be armed/disarmed by the user, but on arming the partition is blocked for a time indicated by the user or determined by the installer (see Default block time option). When blocked, the partition can only be disarmed by the user having the Access to temporary blocked partitions right. An alarm can end the blocking (see Alarm - disarm allowed option).

Follow type “AND” - the partition controlled by status of other partitions. You should indicate the partitions whose status affects the dependent partition. The dependent “AND” type of partition will be armed when all indicated partitions are armed (start of the procedure of arming the last of the indicated partitions will initiate the procedure of arming the dependent partition). The dependent “AND” type of partition will be disarmed when any of the indicated partitions is disarmed. This type of partition is recommended in case of shared corridors.

Follow type “OR” - the partition controlled by status of other partitions. You should indicate the partitions whose status affects the dependent partition. The dependent “OR” type of partition will be armed when any of the indicated partitions is armed (start of the procedure of arming any of the indicated partitions will initiate the procedure of arming the dependent partition). The dependent “OR” type of partition will be disarmed when all indicated partitions are disarmed.

Note: The “AND” or “OR” type dependent partition cannot be controlled by other partitions of the “AND” or “OR” type.

Access according to timer 1...32 / Access according to timer 33...64 - the partition can be armed/disarmed by the user, but only within the time intervals set by the indicated timers.

Controlled by timer 1...32 / Controlled by timer 33...64 - the partition, which is armed in time periods determined by selected timers, but may also be controlled by the user code.

Bank vault - the partition can be armed / disarmed by the user. Disarming may be delayed by a defined period of time (see: Disarm delay). After it has been disarmed, the partition can be automatically re-armed after a defined period of time elapses (see: Time to re-arm).

###### Times

Infinite exit delay - if this option is enabled, the partition will be armed after entering the code and then:

- violating the 86. Entry/Exit - final, 87. Exit - final or 89. Finishing exit delay type zone,

- shortening of the exit delay time by the user (see Exit delay clearing option).

If partition is not armed within 260 seconds, the “Arming failed” event will be registered to the control panel memory. With the option enabled, the Partition exit delay will be taken into account, if the partition is armed using a zone or timer.

Partition exit delay - the time counted from the start of the procedure of arming (by the user, timer, zone, etc.), which allows to leave the protected area without triggering an alarm.

Auto-arming delay - the time counted before starting the procedure of arming by timer. It allows the user to postpone or cancel the auto-arming.

Alarm verification time - the time counted from the triggering alarm by a zone included in alarm verification (with enabled Pre-alarm or With verification option). If during the count another zone included in the alarm verification triggers an alarm, a verified alarm will be triggered.

Audible alarm after verification - if this option is enabled, the alarms from zones with the Pre-alarm or With verification option enabled will only trigger loud alarm signaling after verification. The unverified alarms will not trigger loud alarm signaling.

Guard round (on armed) every - the maximum period of time that can elapse since the last guard round when the partition is armed. If the time is exceeded, information about the lack of guard round will be saved to the control panel memory. Programming the value 0 will disable the control of guard round.

Guard round (on disarmed) every - the maximum period of time that can elapse since the last guard round when the partition is disarmed. If the time is exceeded, information about the lack of guard round will be saved to the control panel memory. Programming the value 0 will disable the control of guard round.

Blocked for guard round - the time counted from the moment of registering the guard round, during which the partition is blocked.

Cash machine block delay - the time counted from the moment of entering the user code of the Cash machine zones bypassing type. After expiry of this time, the 24h Cash machine type zones will be bypassed.

Cash machine block time - the time during which the 24h Cash machine type zones will be bypassed after entering the user code of the Cash machine zones bypassing type. The bypass can be delayed by the Cash machine block delay.

Disarm delay - the parameter applies to the Bank vault partition type. The partition will only be disarmed after a defined period of time has elapsed since the code was used by the user. If the time is equal to 0, the partition will be disarmed immediately.

Time to re-arm - the parameter applies to the Bank vault partition type. After disarming, the control panel will be analyzing for a defined period of time whether a door in the partition will be opened by means of an access control module (partition keypad, code lock, etc.). If the door is not opened, the partition will be automatically re-armed (the partition exit delay countdown will not be running). If the time value is equal to 0, the partition will not be re-armed. Irrespective of the preset value, if the Disarm delay parameter is 0, the partition will not be re-armed.

###### Options

Arm by two codes - if this option is enabled, arming requires that codes be entered in turn by two users.

Disarm by two codes - if this option is enabled, disarming requires that codes be entered in turn by two users.

Codes on two keypads - if this option is enabled and the partition is armed/disarmed using two codes, they must be entered from different keypads.

Valid within 30 sec - if this option is enabled and two codes are required for arming/disarming, the second user has to enter the code within 30 seconds of entering the code by the first user.

Timer priority - if this option is enabled, arming/disarming is always done by the timer. If this option is disabled, the timer will disarm the partition if it was armed by the timer (if it was armed by the user, the timer will not disarm the partition).

Exit delay clearing - if this option is enabled, you can reduce the exit delay countdown by entering 9# from the keypad/partition keypad. The partition will be armed immediately. The exit delay clearing is only available from the same keypad/partition keypad, from which the partition was armed (the Exit delay clearing enable option must be enabled in the keypad).

Default block time - the option applies to the With temporary blocking partition type. If the option is enabled and the Default part. block time is preset, the partition will be blocked on arming for a default time period, as defined by the installer (the blocking time cannot be programmed by the user).

Alarm - disarm allowed - the option applies to the With temporary block partition type. During alarm, the partition can be disarmed by the users who do not have the Access to temporary blocked partitions right.

###### Buttons

Timers - click to open Timers window. The button is available, if the partition is controlled by timer.

Partition timer - click to open Timer of partition window. The button is available when the DLOADX program is communicating with the control panel.

Creating new partition

Removal of the partition

Adding zone to partition

Removal of the zone from the partition

#### Creating new partition

- In the Structure window, System tab, click on the branch with the name of object in which you want to create a new partition.

- Click on the Add button. A new partition will be created.

- Click on the , to write the changes to the control panel.

#### Removal of the partition

- In the Structure window, System tab, click on the branch with the name of partition you want to remove.

- Click on the Delete button. The Confirm window will open.

- Click on the Yes button. The Confirm window will close and the partition will be removed.

- Click on the , to write the changes to the control panel.

#### Adding zone to partition

- In the Structure window, System tab, right click on the branch with the name of partition to which you want to assign a zone. Context menu will be displayed.

- Move the cursor over Add ZONE. A list of available zones will be displayed.

- Click on the zone to assign it to the partition.

- Click on the , to write the changes to the control panel.

#### Removal of the zone from the partition

- In the Structure window, System tab, click on the branch with the name of zone you want to remove.

- Click on the Delete button. The Confirm window will open.

- Click on the Yes button. The Confirm window will close and the zone will be removed.

- Click on the , to write the changes to the control panel.

#### Timer of partition

In each partition you can configure a timer which will automatically arm and/or disarm that partition.

-----------------------------------------------------------

Timer active - if the option is enabled, the partition timer will arm / disarm the partition.

day - select if partition is to be armed / disarmed at different times on different days of the week.

week - select if partition is to be armed / disarmed at the same time everyday.

On - time of arming (hour:minutes).

Off - time of disarming (hour:minutes).

Type - arming type. Enter one of the following digits:

0 - full arming,

1 - full arming + bypasses,

2 - arming without interior,

3 - arming without interior and without entry delay.

###### Buttons

Write to INTEGRA - click to write the partition timer settings to the control panel (they are not written when you click on the  button in the main menu).

Close - click to close the window.

### Partitions settings printout

A table with information about partitions is displayed in the window.

-----------------------------------------------------------

Do not print empty/not used items - if the option is enabled, blank table rows will not be printed.

###### Buttons

Print - click to print information about partitions.

Cancel - click to close the window.

## Hardware

In the tab you can configure the settings of:

- control panel mainboard,

- devices connected to communication buses of control panel,

- virtual keypads applicable in programs and applications intended for configuration and management of the alarm system.

The system structure is displayed in tree form. Click on any element of the tree to start programming it.

Mainboard

Keypad bus

Expansion modules bus

### Mainboard

EOL resistance value - the value of end-of-line resistors for mainboard zones. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

The value of EOL resistors programmed for the mainboard zones applies also to the zones in the keypads:

- INT-KLCD and INT-KLCDR with electronics version 3.2 and firmware version 2.11 (or later),

- INT-KLFR,

- INT-KSG with firmware version 1.02 (or later),

- INT-TSG,

- INT-TSH,

- INT-TSI.

### Keypad bus

Bus short-circuit - Triggers alarm in partition - if this option is enabled, short-circuit in the bus will trigger tamper alarm in the partition you have selected in the field on the right.

Tamper alarm - Always loud signaling - if this option is enabled, a tamper alarm will be always signaled at outputs (if this option is disabled - only if system is armed).

###### Buttons

Keypads identification - click to start the function of identification of devices connected to the keypad bus and wireless keypads enrolled in the ABAX system controllers (Identification).

###### ETHM modules

PING test

The ETHM-1 (firmware version 1.05 or newer) / ETHM-1 Plus modules can test communications by using the PING command sent to the indicated network device. The ETHM-1 / ETHM-1 Plus module will be testing communication after the parameters described below are configured and the PING test option is enabled in the module itself.

Address to test - address of the device to which the module is to send the PING command to test communications. It can be entered as an IP address (4 decimal numbers separated by dots) or as a name.

Period - the interval between consecutive communication tests by using the PING command. If value 0 is programmed, the communication test will be disabled.

Tries no. before trouble - the number of unsuccessful communication tests (the module has received no answer to the PING command sent) after which trouble will be reported. If value 0 is programmed, the communication test will be disabled.

Integration

The ETHM-1 / ETHM-1 Plus module can be used for integration of the alarm control panel with other systems. If the Encrypted integration option is enabled in the module, the communication is encrypted.

Integration encryption key - a string of up to 12 alphanumeric characters (digits, letters and special characters), used for data encryption during communication between the control panel and other systems.

Add - click to open Add module window (the button will be available after you click on a branch which represents bus).

Delete - click to remove the selected device (the button will be available for devices added in the Add module window if the changes have not been written to the control panel).

INT-KLCD

INT-KLCDR

INT-KSG

INT-KWRL

INT-TSG

INT-TSH

INT-TSI

ETHM-1

INT-GSM

ETHM+GSM

CA-64 PTSA

INT-RS

GUARDX on RS-232

GUARDX/INTEGRA CONTROL

DLOADX (RS-232)

DLOADX (modem)

#### INT-KLCD

The following hardwired LCD keypads with mechanical keys are identified as the INT-KLCD:

INT-KLCD,

INT-KLCDK,

INT-KLCDL,

INT-KLCDS.

The keypad enables the control panel to be operated and programmed.

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Note: In the case of the INTEGRA 256 Plus control panel, violation of zone numbers 129 to 256 will be indicated by the keypads with firmware version:

INT-KLCD - 1.12 (or newer),

INT-KLCDK / INT-KLCDL / INT-KLCDS - 6.12 (or newer).

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

LCD backlight - selection of the display backlighting type.

Keys backlight - selection of the keypad backlighting type.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the  LED goes off after all managed by keypad partitions are armed (if the option is disabled, the LED goes off after just one of the partitions is armed).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Show code entering - with this option enabled, entering the code is presented on the keypad display by asterisks.

Show keypad name - with this option enabled, the keypad name is presented in the lower line of the display.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened after pressing in turn the 9# keys.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Displ. mode switching - with the option enabled, you can toggle the display between the standby mode and the partition status display mode by using the 9 key.

Show disarm messages - if this option is enabled, the keypad will inform about disarming with a displayed message at all times. If the option is disabled - only in case of disarming from the given keypad.

Show arm messages - if this option is enabled, the keypad will inform about arming with a displayed message (irrespective of how the system was armed).

Communication RS - if this option is enabled, it is possible to connect a computer with GUARDX program to the keypad RS-232 port. When the option is enabled, the GUARDX on RS-232 branch will appear on the tree representing hardware.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

###### Zones

For each of the keypad zones can be defined whether it will be used or not.

###### Auto-backlight

If the backlight of display or keys is to be turned on automatically, you can define whether and which event will additionally turn on the backlight:

No - backlight will be turned on only when pressing any key.

Viol. of zone - backlight will be additionally turned on when the selected zone is violated.

Entry delay in part. - backlight will be additionally turned on when starting the entry delay countdown in the selected partition.

Note: In the case of the INTEGRA 256 Plus control panel, violation of the zone numbers from 129 to 256 can turn on backlight in the keypads with the following firmware version:

INT-KLCD - 1.12 (or newer),

INT-KLCDK / INT-KLCDL / INT-KLCDS - 6.12 (or newer).

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

###### Buttons

Copy - click to open Copy window.

Volume/filter

State inspections

User functions definition

##### Volume/filter

Note: You can adjust the volume level for INT-KLCD keypad.

Volume - volume level of the beeps generated during keypad operation (key pressing, confirmation of performed operation, etc.).

Volume - chime - volume level of the beeps generated after zone violation (CHIME).

Volume - entry delay - volume level of the entry delay beeps.

Volume - exit delay - volume level of the exit delay beeps.

Volume - fire - volume level of the fire alarm beeps.

Volume - alarm - volume level when signaling burglary, panic and medical alarms

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

###### Permanently displayed partitions

You can select the partitions whose state will be permanently presented in the lower line of the display. Up to 16 partitions can be selected. The partitions are displayed successively: for example, if the partitions 3, 6 and 7 are selected, their state will be displayed in the first, second and third position of the display.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key.

#### INT-KLCDR

The following hardwired LCD keypads with mechanical keys and built-in proximity card reader are identified as the INT-KLCDR:

INT-KLCDR,

INT-KLFR.

The keypad enables the control panel to be operated and programmed.

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Note: In the case of the INTEGRA 256 Plus control panel, violation of zone numbers 129 to 256 will be indicated by the INT-KLFR keypads and the INT-KLCDR keypads with firmware version 1.12 (or newer).

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

LCD backlight - selection of the display backlighting type.

Keys backlight - selection of the keypad backlighting type.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the  LED goes off after all managed by keypad partitions are armed (if the option is disabled, the LED goes off after just one of the partitions is armed).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Show code entering - with this option enabled, entering the code is presented on the keypad display by asterisks.

Show keypad name - with this option enabled, the keypad name is presented in the lower line of the display.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened after pressing in turn the 9# keys.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Displ. mode switching - with the option enabled, you can toggle the display between the standby mode and the partition status display mode by using the 9 key.

Show disarm messages - if this option is enabled, the keypad will inform about disarming with a displayed message at all times. If the option is disabled - only in case of disarming from the given keypad.

Show arm messages - if this option is enabled, the keypad will inform about arming with a displayed message (irrespective of how the system was armed).

Communication RS - if this option is enabled, it is possible to connect a computer with GUARDX program to the keypad RS-232 port. When the option is enabled, the GUARDX on RS-232 branch will appear on the tree representing hardware.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

###### Zones

For each of the keypad zones can be defined whether it will be used or not.

###### Auto-backlight

If the backlight of display or keys is to be turned on automatically, you can define whether and which event will additionally turn on the backlight:

No - backlight will be turned on only when pressing any key.

Viol. of zone - backlight will be additionally turned on when the selected zone is violated.

Entry delay in part. - backlight will be additionally turned on when starting the entry delay countdown in the selected partition.

Note: In the case of the INTEGRA 256 Plus control panel, violation of the zone numbers from 129 to 256 can turn on backlight in the INT-KLFR keypads and INT-KLCDR keypads with the firmware version 1.12 (or newer).

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

###### Buttons

Copy - click to open Copy window.

Volume/filter

State inspections

User functions definition

Proximity cards

##### Volume/filter

Volume - volume level of the beeps generated during keypad operation (key pressing, confirmation of performed operation, etc.).

Volume - chime - volume level of the beeps generated after zone violation (CHIME).

Volume - entry delay - volume level of the entry delay beeps.

Volume - exit delay - volume level of the exit delay beeps.

Volume - fire - volume level of the fire alarm beeps.

Volume - alarm - volume level when signaling burglary, panic and medical alarms

Card reader filter - the level of signal filtering by the proximity card reader. Higher filtering level is useful where noise occurs, causing the reader to malfunction.

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

###### Permanently displayed partitions

You can select the partitions whose state will be permanently presented in the lower line of the display. Up to 16 partitions can be selected. The partitions are displayed successively: for example, if the partitions 3, 6 and 7 are selected, their state will be displayed in the first, second and third position of the display.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key.

##### Proximity cards

###### Card function

Card read - you can select the function executed after presenting the card.

Card holddown - you can select the function executed after holding the card.

Door - if presenting the card or holding it is to open a door, you must indicate the door supervised by the access control module or the 101. Card read - expander type output.

###### Wrong card

Signal on wrong card - if this option is enabled, reading in an unknown card will be signaled by two long beeps.

Event after 3 readings - if this option is enabled, reading in an unknown card three times will save the event.

Alarm after 3 readings - if this option is enabled, reading in an unknown card three times will trigger an alarm. The option is available, if the Event after 3 readings option is enabled.

###### Code+card

Code OR card - the user can use code or card for authentication.

Code AND card - the user must use code and card for authentication.

Follow output - the authentication method depends on the status of selected output (the output active - code and card; the output inactive - code or card).

Notes:

In case of the authentication using code and card, the executed function depends on the second identifier.

The outputs 255 and 256 cannot be used for controlling the authentication method.

#### INT-KSG

INT-KSG - hardwired LCD keypad with touch keys.

The keypad enables the control panel to be operated and programmed.

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Note: In the case of the INTEGRA 256 Plus control panel, violation of zone numbers 129 to 256 will be indicated by the INT-KSG keypads with firmware version 2.00 (or newer).

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

LCD backlight - selection of the display backlighting type.

Keys backlight - selection of the keypad backlighting type.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, touching and holding the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, touching and holding the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, touching and holding the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Sign. exit delay - with this option enabled, the keypad will audibly signal the exit delay countdown.

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the  LED goes off after all managed by keypad partitions are armed (if the option is disabled, the LED goes off after just one of the partitions is armed).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Show code entering - with this option enabled, entering the code is presented on the keypad display by asterisks.

Show keypad name - with this option enabled, the keypad name is presented in the lower line of the display.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened after pressing in turn the 9# keys.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Displ. mode switching - with the option enabled, you can toggle the display between the standby mode and the partition status display mode by using the 9 key.

Show disarm messages - if this option is enabled, the keypad will inform about disarming with a displayed message at all times. If the option is disabled - only in case of disarming from the given keypad.

Show arm messages - if this option is enabled, the keypad will inform about arming with a displayed message (irrespective of how the system was armed).

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

###### Zones

For each of the keypad zones can be defined whether it will be used or not.

###### Auto-backlight

If the backlight of display or keys is to be turned on automatically, you can define whether and which event will additionally turn on the backlight:

No - backlight will be turned on only when pressing any key.

Viol. of zone - backlight will be additionally turned on when the selected zone is violated.

Entry delay in part. - backlight will be additionally turned on when starting the entry delay countdown in the selected partition.

Note: In the case of the INTEGRA 256 Plus control panel, violation of the zone numbers from 129 to 256 can turn on backlight in the INT-KSG keypads with the firmware version 2.00 (or newer).

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

###### Buttons

Copy - click to open Copy window.

Volume/filter

State inspections

User functions definition

Macro Commands

Status screen

##### Volume/filter

Volume - volume level of the beeps generated during keypad operation (key pressing, confirmation of performed operation, etc.).

Volume - chime - volume level of the beeps generated after zone violation (CHIME).

Volume - entry delay - volume level of the entry delay beeps.

Volume - exit delay - volume level of the exit delay beeps.

Volume - fire - volume level of the fire alarm beeps.

Volume - alarm - volume level when signaling burglary, panic and medical alarms

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

###### Permanently displayed partitions

You can select the partitions whose state will be permanently presented in the lower line of the display. Up to 16 partitions can be selected. The partitions are displayed successively: for example, if the partitions 3, 6 and 7 are selected, their state will be displayed in the first, second and third position of the display.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key.

##### Macro Commands

Before making any changes, click on the Read button, and after making the changes - on the Write button. The macro command related data are stored in the keypad and are not read / written when you click on the  /  button in the main menu.

###### Groups

The macro commands which are to be available for the keypad users must be assigned to one of the four groups. Up to 16 macro commands can be assigned to a group. The groups of macro commands and macro commands assigned to them are presented in a tree form.

Name - macro command group name presented at the bottom of the display above the  key (up to 8 characters).

Add macro - the button is available after you click on a group of macro commands. It displays a list containing the names of defined macro commands. After you click on a name, the macro command will be added to the group.

Remove macro - the button is available after you click on any macro command. It removes that macro command from the group.

- click to move the highlighted macro command down within the group.

- click to move the highlighted macro command up within the group.

Export to file - click to export defined macro commands to a file.

Import from file - click to import macro commands from a file.

###### Definitions

The macro command is a sequence of actions, composed of single commands, which are to be done by the control panel when running the macro command.

New macro - click to create a new macro command.

Remove macro - click to delete selected macro command.

Name - individual name of the macro command (up to 32 characters).

Code - the code which is to be used for authorization when executing commands contained in the macro command. For execution of such commands to be possible, the code must be granted a suitable authority level. It is presented as a string of asterisks.

Note: If, when running a macro command, it turns out that the code is invalid (e.g. it has been changed in the meantime), the user will be able to enter the correct code. It will be automatically saved to the keypad memory (replacing the invalid one).

Authorization required - if this option is enabled, the macro command will only be run after user authorization by using a code. The code entered in the Code field will be ignored.

Disabled if armed - if this option is enabled, the macro command will not be available, when any of the partitions operated by the keypad is armed.

Autoexecute - if this option is enabled and the group contains just one macro command, the macro command will run immediately on touching the  key (if the Authorization required option is enabled, authorization with code will be necessary).

Commands list - commands assigned to the currently highlighted macro command. The  and  buttons allow you to change the order of commands (moving the selected command up and down).

Add - click to add to the list a new command, selected in the Command field.

Change - click to save the changes to the command parameters which were made after adding the command to the list (otherwise, the changes made will not be saved).

Delete - click to remove the highlighted command from the list.

Command - the control panel executed function which can be assigned to the macro command. The list of all available functions will be displayed after you click the  button. Depending on which function you choose:

Arming - select the partitions which are to be armed (double-click on the field designated by the partition number) and define the arming mode (next clicks on the field designated by the partition number; the digit inside the field has the following meaning: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay).

Disarming - select the partitions which are to be disarmed (double-click on the field designated by the partition number).

Alarm clearing - select the partitions in which alarm is to be cleared (double-click on the field designated by the partition number).

Bypass zones - select the zones which are to be inhibited (double-click on the field designated by the zone number).

Unbypass zones - select the zones which are to be unbypassed (double-click on the field designated by the zone number).

Outputs ON - select the outputs which are to be activated (double-click on the field designated by the output number).

Outputs OFF - select the outputs which are to be deactivated (double-click on the field designated by the output number).

Change outputs state - select the outputs whose status is to be changed (double-click on the field designated by the output number).

KNX telegram - program the following parameters of KNX telegram for the INT-KNX module:

INT-KNX module - INT-KNX module which is to send the telegram.

Group address - the group address which will be inserted in the telegram.

Type - the telegram type.

Value - the value that will be inserted in the telegram (parameter available for some types of the telegram).

Priority - telegram priority (if two elements of the bus start transmitting simultaneously, the telegram with higher priority will be sent first).

KNX telegram (v2) - program the following parameters related to setting the value of KNX communication object:

Module INT-KNX - INT-KNX-2 module in which the value is to be set.

Macro Command - name of the Virtual (macro) type object, defined in INT-KNX-2 module.

Data type - size and meaning of the communication object data defined in INT-KNX-2 module for selected object.

Value - value to be set (if the type of data provides for sending a sequence of characters, you can enter up to 13 characters).

Exit delay clearing (no additional parameters to configure).

Notes:

The partitions must be controlled by user code.

The zones must not have the Bypass disabled option enabled.

The outputs must be the 24. MONO Switch, 25. BI Switch, 105. Shutter up, 106. Shutter down or Remote switch type (they need not be assigned to any group of outputs).

The keypad can be used to control the KNX system, if the INT-KNX or INT-KNX-2 module is connected to the control panel.

###### Buttons

Read - click to read the macro command related data from the keypad.

Write - click to write the macro command related data to the keypad.

Quit - click to cancel reading or writing the macro command related data.

Reset - click to restore keypad factory settings (after the factory settings have been restored, click on Read, to read data from the keypad).

Defining the macro commands

##### Defining the macro commands

- Click on the Read button to read the macro command related data from the keypad.

- Click the Definitions tab.

- Click the New macro button. A new macro command will appear in the list.

- Enter a name for the new macro command.

- If the macro command is to be run without entering the code by the user, enter the code with a suitable authority level.

- If running the macro command is to be each time preceded by user authorization, enable the Authorization required option.

- If the macro command is not to be available, when any of the partitions operated by the keypad is armed, enable the Disabled if armed option.

- If the macro command is to be run instantly on touching , enable the Autoexecute option (if so, only this single macro command is to be assigned to the group).

- Click on the  button in the Command field and select from the list the function the new macro command is to execute.

- Configure the command parameters as required.

- Click the Add button. A new command will appear in the list of commands assigned to the macro command. After clicking the command you can still make a correction of its parameters. After making the changes, click the Change button.

- Repeat the steps 9-11, if you want to add next commands.

- Click the Groups tab.

- Click the group to be edited.

- Enter the group name.

- Click the Add macro button. A list of all defined macro commands will be displayed.

- Click on a macro command to add it to the group. The macro command will be put in the tree under the group.

- Click on the Write button to write the macro command related data to the keypad.

##### Status screen

Before making any changes, click on the Read button, and after making the changes - on the Write button. The status screen related data are stored in the keypad and are not read / written when you click on the  /  button in the main menu.

The status screen is displayed automatically after the keypad is idle for 60 seconds. The following information can be displayed on the status screen:

any text,

partition status by means of symbols (select individual partitions whose status will be displayed),

zone status by means of symbols (select individual zones whose status will be displayed),

output status by means of symbols (select individual outputs whose status will be displayed),

temperature (indicate the control panel zone to which the temperature detector is assigned, and define whether the temperature is to be displayed in Celsius or Fahrenheit degrees),

date and time (particular elements, such as day, month, year, hour, minutes and seconds are to be configured individually),

keypad name,

zone status by means of messages (select individual zones whose status will be displayed, and define the content and color of messages for normal state and for violation, because only these two states are presented in the form of message),

output status by means of messages (select individual outputs whose status will be displayed, and define the content and color of messages for active and inactive output).

There are two font sizes available for use on the status screen. Using the “drag and drop” method, you can easily select the place where the given information will be presented on the display.

###### Buttons

- click to move the selected element up in the list.

- click to move the selected element down in the list.

Add - click to place on the status screen the information selected in the field above.

Delete - click to remove from the status screen the selected information.

Read - click to read the data from the keypad.

Write - click to write the data to the keypad.

Quit - click to terminate data reading/writing.

#### INT-KWRL

INT-KWRL - wireless LCD keypads with mechanical keys.

The keypad enables the control panel to be operated and programmed.

The wireless keypad can work in two modes:

active mode - the keypad operation is similar to that of the wired LCD keypad (the display is on; backlight, LED indication and sound signaling are enabled). The active mode is started by pressing any key. Additionally, the active mode can be started automatically when an alarm occurs or an entry delay, an exit delay or an auto-arming delay begins (see description of the Wake-up parameter - INT-KWRL).

inactive mode - the keypad saves batteries life (the display is off; backlight, LED indication and sound signaling are disabled - the CHIME signal will sound if a time different from 0 is preset for the Wake-up parameter). The inactive mode is started:

- after 20 seconds since the last key press,

- after preset time, if the active mode was started automatically (see description of the Wake-up parameter - INT-KWRL).

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Note: The wireless keypad signals the CHIME from zones not more frequently than once every 30 seconds. In the inactive mode, the CHIME from zones is only signaled if a value different from 0 is preset for the Wake-up parameter.

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

LCD backlight - the way how the display backlight will work in the active mode:

not present - disabled,

permanent 50% - enabled: brightness 50%,

permanent 100% - enabled: brightness 100%,

auto 0-50% - enabled: brightness 50%,

auto 0-100% - enabled: brightness 100%,

auto 50%-100% - enabled: brightness 100%.

Keys backlight - the way how the keys backlight will work in the active mode:

not present - disabled,

auto - enabled,

permanent - enabled.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the  LED goes off after all managed by keypad partitions are armed (if the option is disabled, the LED goes off after just one of the partitions is armed).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Show code entering - with this option enabled, entering the code is presented on the keypad display by asterisks.

Show keypad name - with this option enabled, the keypad name is presented in the lower line of the display.

Exit delay clearing enable - if this option is enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened after pressing in turn the   keys.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Show disarm messages - if this option is enabled, the keypad displays the disarming message irrespective of how the system has been disarmed. If this option is disabled, the keypad displays the disarming message only when the system has been disarmed from this keypad.

Show arm messages - if this option is enabled, the keypad displays the arming message. If the option is disabled, the arming message is not displayed.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the   keys (without the need to enter the user code).

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

###### Buttons

Copy - click to open Copy window.

Volume/filter

State inspections

User functions definition

Proximity cards

##### Volume/filter

Volume - volume level of the beeps generated during keypad operation (key pressing, confirmation of performed operation, etc.).

Volume - chime - volume level of the beeps generated after zone violation (CHIME).

Volume - entry delay - volume level of the entry delay beeps.

Volume - exit delay - volume level of the exit delay beeps.

Volume - fire - volume level of the fire alarm beeps.

Volume - alarm - volume level when signaling burglary, panic and medical alarms

Card reader filter - the level of signal filtering by the proximity card reader. Higher filtering level is useful where noise occurs, causing the reader to malfunction.

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the  key.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the  key.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the  key.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the  key.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the  key.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the  key.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

###### Permanently displayed partitions

You can select the partitions whose state will be permanently presented in the lower line of the display. Up to 16 partitions can be selected. The partitions are displayed successively: for example, if the partitions 3, 6 and 7 are selected, their state will be displayed in the first, second and third position of the display.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key.

##### Proximity cards

###### Card function

Card read - you can select the function executed after presenting the card.

Card holddown - you can select the function executed after holding the card.

Door - if presenting the card or holding it is to open a door, you must indicate the door supervised by the access control module or the 101. Card read - expander type output.

###### Wrong card

Signal on wrong card - if this option is enabled, reading in an unknown card will be signaled by two long beeps.

Event after 3 readings - if this option is enabled, reading in an unknown card three times will save the event.

Alarm after 3 readings - if this option is enabled, reading in an unknown card three times will trigger an alarm. The option is available, if the Event after 3 readings option is enabled.

###### Code+card

Code OR card - the user can use code or card for authentication.

Code AND card - the user must use code and card for authentication.

Follow output - the authentication method depends on the status of selected output (the output active - code and card; the output inactive - code or card).

Notes:

In case of the authentication using code and card, the executed function depends on the second identifier.

The outputs 255 and 256 cannot be used for controlling the authentication method.

#### INT-TSG

INT-TSG - hardwired touchscreen keypad.

The keypad enables the control panel to be operated and programmed.

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the way the time and date are displayed on the keypad main screen and on the terminal.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, the fire alarm can be triggered from the keypad by tapping and holding for 3 seconds:

-  on the “Emergency” screen,

-  on the terminal.

PANIC - if this option is enabled, the panic alarm can be triggered from the keypad by tapping and holding for 3 seconds:

-  on the “Emergency” screen,

-  on the terminal.

AUX. - if this option is enabled, the medical alarm can be triggered from the keypad by tapping and holding for 3 seconds:

-  on the “Emergency” screen,

-  on the terminal.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal). Additionally, the silent panic alarm can be triggered by tapping and holding any part of the status screen for about 3 seconds. The option is available, if the PANIC option is enabled.

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - when this option is enabled, tapping the keypad screen is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the  LED goes off after all managed by keypad partitions are armed (if the option is disabled, the LED goes off after just one of the partitions is armed).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Show code entering - with this option enabled, entering the code is presented on the keypad display by asterisks.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened by means of:

- macro command;

- terminal (after tapping in turn the  and  keys).

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Show disarm messages - if this option is enabled, the keypad will inform about disarming with a displayed message at all times. If the option is disabled - only in case of disarming from the given keypad.

Show arm messages - if this option is enabled, the keypad will inform about arming with a displayed message (irrespective of how the system was armed).

Quick control - if this option is enabled, the Outs control user function can be started without entering the user code:

- after tapping the  icon on the main screen, if no macro command is assigned to the group;

- after tapping and holding the  icon on the main screen for about 3 seconds, if at least one macro command is assigned to the group;

- from the terminal, after you tap in turn the  and  keys.

###### Zones

For each of the keypad zones can be defined whether it will be used or not.

###### Auto-backlight

The keypad can be woken up after occurrence of a specified event in the system: starting the entry delay countdown in a selected partition, or violating a selected zone.

###### Wake-up

You can define how the keypad will respond to the wake-up (after a tap on the screen by the user or occurrence of a specified event in the system):

Status screen - status screen will be displayed.

Menu screen - main screen will be displayed.

Disarming - if at least one partition managed by the keypad is armed, the authorization screen will be displayed (after entering the code and tapping , and depending on the system state: the partition(s) will be disarmed / partition selection screen will be displayed / “Alarm clearing / Disarming” screen will be displayed). If none of the partitions is armed, the main screen will be displayed.

Photo frame - if this option is enabled, the following will be displayed after 10 minutes of keypad inactivity:

slide show - if there are at least two pictures on the memory card and the value of Change picture every parameter is different from 0,

clock - if there are one or no pictures on the memory card or the value of Change picture every parameter is 0.

If this option is disabled, the screen will go blank after 10 minutes of keypad inactivity.

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

###### Buttons

Copy - click to open Copy window.

State inspections

User functions definition

Macro Commands

Status screen

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

4 - partitions armed - if this option is enabled, the user can inspect the partition state:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

5 - alarm events memory - if this option is enabled, the user can view the alarms log:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

6 - trouble memory - if this option is enabled, the user can view the troubles log:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

7 - trouble status - if this option is enabled, the user can view the current troubles:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by tapping and holding for 3 seconds  on the terminal.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the terminal.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the terminal.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and tapping the selected arrow key on the terminal.

##### Macro Commands

Before making any changes, click on the Read button, and after making the changes - on the Write button. The macro command related data are stored in the keypad and are not read / written when you click on the  /  button in the main menu.

Note: In the keypad with factory default settings, there are two macro commands defined which are assigned to the first group:

0# - quick full arming (the control panel will only execute the macro command after you define the partitions which are to be armed in the event of quick full arming);

9# - exit delay clearing (the control panel will execute the macro command if reducing the exit delay time is allowed by the partition settings and the Exit delay clearing enable option is enabled in the keypad).

###### Groups

The macro commands which are to be available for the keypad users must be assigned to one of the four groups. Up to 16 macro commands can be assigned to a group. Up to 6 macro command icons can be displayed on the keypad screen at the same time. The groups of macro commands and macro commands assigned to them are presented in a tree form.

Name - name of the macro command group which is displayed on the keypad screen under the icon (up to 16 characters in two lines, up to 8 characters in the line). Do not enter the name if it is not to be displayed.

Icon - icon of a group of macro commands. In order to display the list of available icons, click the  button.

Macro available on the status screen - if this option is enabled, the group of macro commands is available from the status screen, i.e. touching a corner of the status screen will display macro commands assigned to that group (1st group of macro commands - upper left corner; 2nd group of macro commands - upper right corner; 3rd group of macro commands - lower left corner; 4th group of macro commands - lower right corner).

Icon visible on the status screen - if this option is enabled, the icon of the group of macro commands is displayed in the corresponding corner of the status screen. The option is available when the Macro available on the status screen option is enabled for the group of macro commands.

Add macro - the button is available after you click on a group of macro commands. It displays a list containing the names of defined macro commands. After you click on a name, the macro command will be added to the group.

Remove macro - the button is available after you click on any macro command. It removes that macro command from the group.

- click to move the highlighted macro command down within the group.

- click to move the highlighted macro command up within the group.

Export to file - click to export defined macro commands to a file.

Import from file - click to import macro commands from a file.

###### Definitions

The macro command is a sequence of actions, composed of single commands, which are to be done by the control panel when running the macro command.

New macro - click to create a new macro command.

Remove macro - click to delete selected macro command.

Name - individual name of the macro command (up to 16 characters in two lines, up to 8 characters in the line).

Code - the code which is to be used for authorization when executing commands contained in the macro command. For execution of such commands to be possible, the code must be granted a suitable authority level. It is presented as a string of asterisks.

Note: If, when running a macro command, it turns out that the code is invalid (e.g. it has been changed in the meantime), the user will be able to enter the correct code. It will be automatically saved to the keypad memory (replacing the invalid one).

Authorization required - if this option is enabled, the macro command will only be run after user authorization by using a code. The code entered in the Code field will be ignored.

Disabled if armed - if this option is enabled, the macro command will not be available, when any of the partitions operated by the keypad is armed.

Autoexecute - if this option is enabled and the group contains just one macro command, the macro command will run immediately on tapping the icon of macro command group (or the status screen corner, if the Macros available on the status screen option is enabled). If the Authorization required option is enabled, authorization with code will be necessary.

No confirmation messages - if this option is enabled, no messages will appear to inform you about execution of a command or an error after running a macro command (the screen from which the macro command was run will still be displayed).

Icon - the macro command icon. The list of available icons will be displayed after you click the  button. If the State follow output option is enabled, select 2 icons for the macro commands. One icon will be displayed when the output is inactive, and the other - when the output is active.

State follow output - if this option is enabled, the icon of macro command will change depending on the status of output whose number should be selected in the field on the right side. Select an output, the status of which depends on the actions taken by the control panel after running the macro command. Thus it will be possible to inform the user by means of macro command icons about, for example, the status of outputs controlled by using macro commands or the status of partitions which are armed by a macro command.

Show name - if this option is enabled, the macro command name will be displayed on the keypad below the icon.

Commands list - commands assigned to the currently highlighted macro command. The  and  buttons allow you to change the order of commands (moving the selected command up and down).

Add - click to add to the list a new command, selected in the Command field.

Change - click to save the changes to the command parameters which were made after adding the command to the list (otherwise, the changes made will not be saved).

Delete - click to remove the highlighted command from the list.

Command - the control panel executed function which can be assigned to the macro command. The list of all available functions will be displayed after you click the  button. Depending on which function you choose:

Arming - select the partitions which are to be armed (double-click on the field designated by the partition number) and define the arming mode (next clicks on the field designated by the partition number; the digit inside the field has the following meaning: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay).

Disarming - select the partitions which are to be disarmed (double-click on the field designated by the partition number).

Alarm clearing - select the partitions in which alarm is to be cleared (double-click on the field designated by the partition number).

Bypass zones - select the zones which are to be inhibited (double-click on the field designated by the zone number).

Unbypass zones - select the zones which are to be unbypassed (double-click on the field designated by the zone number).

Outputs ON - select the outputs which are to be activated (double-click on the field designated by the output number).

Outputs OFF - select the outputs which are to be deactivated (double-click on the field designated by the output number).

Change outputs state - select the outputs whose status is to be changed (double-click on the field designated by the output number).

KNX telegram - program the following parameters of KNX telegram for the INT-KNX module:

INT-KNX module - INT-KNX module which is to send the telegram.

Group address - the group address which will be inserted in the telegram.

Type - the telegram type.

Value - the value that will be inserted in the telegram (parameter available for some types of the telegram).

Priority - telegram priority (if two elements of the bus start transmitting simultaneously, the telegram with higher priority will be sent first).

KNX telegram (v2) - program the following parameters related to setting the value of KNX communication object:

Module INT-KNX - INT-KNX-2 module in which the value is to be set.

Macro Command - name of the Virtual (macro) type object, defined in INT-KNX-2 module.

Data type - size and meaning of the communication object data defined in INT-KNX-2 module for selected object.

Value - value to be set (if the type of data provides for sending a sequence of characters, you can enter up to 13 characters).

Exit delay clearing (no additional parameters to configure).

Quick arm - select the arming mode which is to be activated.

Notes:

The partitions must be controlled by user code.

The zones must not have the Bypass disabled option enabled.

The outputs must be the 24. MONO Switch, 25. BI Switch, 105. Shutter up, 106. Shutter down or Remote switch type (they need not be assigned to any group of outputs).

The keypad can be used to control the KNX system, if the INT-KNX or INT-KNX-2 module is connected to the control panel.

###### Buttons

Read - click to read the macro command related data from the keypad.

Write - click to write the macro command related data to the keypad.

Quit - click to cancel reading or writing the macro command related data.

Reset - click to restore keypad factory settings (after the factory settings have been restored, click on Read, to read data from the keypad).

Defining the macro commands

##### Defining the macro commands

- Click on the Read button to read the macro command related data from the keypad.

- Click the Definitions tab.

- Click the New macro button. A new macro command will appear in the list.

- Enter a name for the new macro command.

- If the macro command name is to be displayed on the keypad, enable the Show name option.

- If the macro command is to be run without entering the code by the user, enter the code with a suitable authority level.

- If running the macro command is to be each time preceded by user authorization, enable the Authorization required option.

- If the macro command is not to be available, when any of the partitions operated by the keypad is armed, enable the Disabled if armed option.

- If the macro command is to be run instantly on tapping the icon of macro command group, enable the Autoexecute option (if so, only this single macro command is to be assigned to the group).

- If the confirmation messages are not to be displayed after running the macro command, enable the No confirmation messages option.

- Select the icon which will be used to present the macro command on the keypad.

- If the icon is to change depending on the selected output state:

- enable the State follow output option;

- indicate the output number;

- select the icons which will illustrate inactive and active status of the output.

- Click on the  button in the Command field and select from the list the function the new macro command is to execute.

- Configure the command parameters as required.

- Click the Add button. A new command will appear in the list of commands assigned to the macro command. After clicking the command you can still make a correction of its parameters. After making the changes, click the Change button.

- Repeat the steps 13-15, if you want to add next commands.

- Click the Groups tab.

- Click the group to be edited.

- Enter the group name, if it is to be displayed on the keypad.

- Select the icon which will be used to present the group of macro commands on the keypad.

- Enable the Macro available on the status screen option for the group, if macro commands assigned to the group are to be displayed after touching a corner of the status screen.

- Enable the Icon visible on the status screen option for the group, if the group icon is to be displayed in a corner of the status screen.

- Click the Add macro button. A list of all defined macro commands will be displayed.

- Click on a macro command to add it to the group. The macro command will be put in the tree under the group.

- Click on the Write button to write the macro command related data to the keypad.

##### Status screen

Before making any changes, click on the Read button, and after making the changes - on the Write button. The status screen related data are stored in the keypad and are not read / written when you click on the  /  button in the main menu.

Note: If the Icon visible on the status screen option is enabled for a group of macro commands, do not place any elements in the screen corner where the icon will be displayed, or they will be covered by the icon. The DLOADX program indicates using appropriate graphic symbols the screen corners where the icons will be displayed.

The status screen is displayed automatically after the keypad is idle for 60 seconds. This rule does not apply if the terminal is running. In such a case, the status screen may be displayed later or even will not be displayed at all (e.g. when the service menu is open). The following information can be displayed on the status screen:

any text,

partition status by means of symbols (select individual partitions whose status will be displayed),

zone status by means of symbols (select individual zones whose status will be displayed),

output status by means of symbols (select individual outputs whose status will be displayed),

temperature (indicate the control panel zone to which the temperature detector is assigned, and define whether the temperature is to be displayed in Celsius or Fahrenheit degrees),

date and time (particular elements, such as day, month, year, hour, minutes and seconds are to be configured individually),

keypad name,

zone status by means of messages (select individual zones whose status will be displayed, and define the content and color of messages for normal state and for violation, because only these two states are presented in the form of message),

output status by means of messages (select individual outputs whose status will be displayed, and define the content and color of messages for active and inactive output).

There are three font sizes available for use on the status screen. You can also define color of the font to be used. Using the “drag and drop” method, you can easily select the place where the given information will be presented on the display.

Change picture every - the parameter defines how quickly the pictures will change during the slide show. The slide show can be displayed as the status screen background or when the keypad is idle. The photos to be displayed should be stored on a microSD memory. Their size should not exceed 480 x 272 pixels. Only images in BMP format are supported. If the programmed time is 0, the pictures will not change (the first picture stored on the microSD card will be displayed all the time).

###### Buttons

- click to move the selected element up in the list.

- click to move the selected element down in the list.

Add - click to place on the status screen the information selected in the field above.

Delete - click to remove from the status screen the selected information.

Wallpaper - click to select another status screen wallpaper.

Save to SD card - click to save the new wallpaper on the microSD card.

Export to file - click to export the status screen settings to a file.

Import from file - click to import the status screen settings from a file.

Read - click to read the data from the keypad.

Write - click to write the data to the keypad.

Quit - click to terminate data reading/writing.

#### INT-TSH

INT-TSH - hardwired touchscreen keypad.

The keypad enables the control panel to be operated and programmed.

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the way the time and date are displayed on the keypad main screen and on the terminal.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, the fire alarm can be triggered from the keypad by tapping and holding for 3 seconds:

-  on the “Emergency” screen,

-  on the terminal.

PANIC - if this option is enabled, the panic alarm can be triggered from the keypad by tapping and holding for 3 seconds:

-  on the “Emergency” screen,

-  on the terminal.

AUX. - if this option is enabled, the medical alarm can be triggered from the keypad by tapping and holding for 3 seconds:

-  on the “Emergency” screen,

-  on the terminal.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal). Additionally, the silent panic alarm can be triggered by tapping and holding any part of the status screen for about 3 seconds. The option is available, if the PANIC option is enabled.

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - when this option is enabled, tapping the keypad screen is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the trouble information on status bar and on terminal will be hidden upon arming of all partitions operated from the keypad (if the option is disabled, the trouble information will be hidden upon arming of one of the partitions).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Show code entering - with this option enabled, entering the code is presented on the keypad display by asterisks.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened by means of:

- macro command;

- terminal (after tapping in turn the  and  keys).

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Show disarm messages - if this option is enabled, the keypad will inform about disarming with a displayed message at all times. If the option is disabled - only in case of disarming from the given keypad.

Show arm messages - if this option is enabled, the keypad will inform about arming with a displayed message (irrespective of how the system was armed).

Quick control - if this option is enabled, the Outs control user function can be started without entering the user code:

- after tapping the  icon on the main screen, if no macro command is assigned to the group;

- after tapping and holding the  icon on the main screen for about 3 seconds, if at least one macro command is assigned to the group;

- from the terminal, after you tap in turn the  and  keys.

###### Zones

For each of the keypad zones can be defined whether it will be used or not.

###### Auto-backlight

The keypad can be woken up after occurrence of a specified event in the system: starting the entry delay countdown in a selected partition, or violating a selected zone.

###### Wake-up

You can define how the keypad will respond to the wake-up (after a tap on the screen by the user or occurrence of a specified event in the system):

Status screen - status screen will be displayed.

Menu screen - main screen will be displayed.

Disarming - if at least one partition managed by the keypad is armed, the authorization screen will be displayed (after entering the code and tapping , and depending on the system state: the partition(s) will be disarmed / partition selection screen will be displayed / “Alarm clearing / Disarming” screen will be displayed). If none of the partitions is armed, the main screen will be displayed.

Photo frame - if this option is enabled, the screen will not go blank after the keypad is idle for 10 minutes. If this option is disabled, the screen will go blank after the keypad is idle for 10 minutes. See also the Show clock option, related to the status screen (Status screen).

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

###### Buttons

Copy - click to open Copy window.

State inspections

User functions definition

Macro Commands

Status screen

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

4 - partitions armed - if this option is enabled, the user can inspect the partition state:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

5 - alarm events memory - if this option is enabled, the user can view the alarms log:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

6 - trouble memory - if this option is enabled, the user can view the troubles log:

- after tapping on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

7 - trouble status - if this option is enabled, the user can view the current troubles:

- after tapping  on the “System status” screen,

- after tapping and holding for 3 seconds  on the terminal.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by tapping and holding for 3 seconds  on the terminal.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the terminal.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the terminal.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and tapping the selected arrow key on the terminal.

##### Macro Commands

Before making any changes, click on the Read button, and after making the changes - on the Write button. The macro command related data are stored in the keypad and are not read / written when you click on the  /  button in the main menu.

Note: In the keypad with factory default settings, there are two macro commands defined which are assigned to the first group:

0# - quick full arming (the control panel will only execute the macro command after you define the partitions which are to be armed in the event of quick full arming);

9# - exit delay clearing (the control panel will execute the macro command if reducing the exit delay time is allowed by the partition settings and the Exit delay clearing enable option is enabled in the keypad).

###### Groups

The macro commands which are to be available for the keypad users must be assigned to one of the four groups. Up to 16 macro commands can be assigned to a group. Up to 6 macro command icons can be displayed on the keypad screen at the same time. The groups of macro commands and macro commands assigned to them are presented in a tree form.

Name - name of the macro command group which is displayed on the keypad screen under the icon (up to 16 characters in two lines, up to 8 characters in the line). Do not enter the name if it is not to be displayed.

Icon - icon of a group of macro commands. In order to display the list of available icons, click the  button.

Macro available on the status screen - if this option is enabled, the group of macro commands is available from the status screen, i.e. touching a corner of the status screen will display macro commands assigned to that group (1st group of macro commands - upper left corner; 2nd group of macro commands - upper right corner; 3rd group of macro commands - lower left corner; 4th group of macro commands - lower right corner).

Icon visible on the status screen - if this option is enabled, the icon of the group of macro commands is displayed in the corresponding corner of the status screen. The option is available when the Macro available on the status screen option is enabled for the group of macro commands.

Add macro - the button is available after you click on a group of macro commands. It displays a list containing the names of defined macro commands. After you click on a name, the macro command will be added to the group.

Remove macro - the button is available after you click on any macro command. It removes that macro command from the group.

- click to move the highlighted macro command down within the group.

- click to move the highlighted macro command up within the group.

Export to file - click to export defined macro commands to a file.

Import from file - click to import macro commands from a file.

###### Definitions

The macro command is a sequence of actions, composed of single commands, which are to be done by the control panel when running the macro command.

New macro - click to create a new macro command.

Remove macro - click to delete selected macro command.

Name - individual name of the macro command (up to 16 characters in two lines, up to 8 characters in the line).

Code - the code which is to be used for authorization when executing commands contained in the macro command. For execution of such commands to be possible, the code must be granted a suitable authority level. It is presented as a string of asterisks.

Note: If, when running a macro command, it turns out that the code is invalid (e.g. it has been changed in the meantime), the user will be able to enter the correct code. It will be automatically saved to the keypad memory (replacing the invalid one).

Authorization required - if this option is enabled, the macro command will only be run after user authorization by using a code. The code entered in the Code field will be ignored.

Disabled if armed - if this option is enabled, the macro command will not be available, when any of the partitions operated by the keypad is armed.

Autoexecute - if this option is enabled and the group contains just one macro command, the macro command will run immediately on tapping the icon of macro command group (or the status screen corner, if the Macros available on the status screen option is enabled). If the Authorization required option is enabled, authorization with code will be necessary.

No confirmation messages - if this option is enabled, no messages will appear to inform you about execution of a command or an error after running a macro command (the screen from which the macro command was run will still be displayed).

Icon - the macro command icon. The list of available icons will be displayed after you click the  button. If the State follow output option is enabled, select 2 icons for the macro commands. One icon will be displayed when the output is inactive, and the other - when the output is active.

State follow output - if this option is enabled, the icon of macro command will change depending on the status of output whose number should be selected in the field on the right side. Select an output, the status of which depends on the actions taken by the control panel after running the macro command. Thus it will be possible to inform the user by means of macro command icons about, for example, the status of outputs controlled by using macro commands or the status of partitions which are armed by a macro command.

Show name - if this option is enabled, the macro command name will be displayed on the keypad below the icon.

Commands list - commands assigned to the currently highlighted macro command. The  and  buttons allow you to change the order of commands (moving the selected command up and down).

Add - click to add to the list a new command, selected in the Command field.

Change - click to save the changes to the command parameters which were made after adding the command to the list (otherwise, the changes made will not be saved).

Delete - click to remove the highlighted command from the list.

Command - the control panel executed function which can be assigned to the macro command. The list of all available functions will be displayed after you click the  button. Depending on which function you choose:

Arming - select the partitions which are to be armed (double-click on the field designated by the partition number) and define the arming mode (next clicks on the field designated by the partition number; the digit inside the field has the following meaning: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay).

Disarming - select the partitions which are to be disarmed (double-click on the field designated by the partition number).

Alarm clearing - select the partitions in which alarm is to be cleared (double-click on the field designated by the partition number).

Bypass zones - select the zones which are to be inhibited (double-click on the field designated by the zone number).

Unbypass zones - select the zones which are to be unbypassed (double-click on the field designated by the zone number).

Outputs ON - select the outputs which are to be activated (double-click on the field designated by the output number).

Outputs OFF - select the outputs which are to be deactivated (double-click on the field designated by the output number).

Change outputs state - select the outputs whose status is to be changed (double-click on the field designated by the output number).

KNX telegram - program the following parameters of KNX telegram for the INT-KNX module:

INT-KNX module - INT-KNX module which is to send the telegram.

Group address - the group address which will be inserted in the telegram.

Type - the telegram type.

Value - the value that will be inserted in the telegram (parameter available for some types of the telegram).

Priority - telegram priority (if two elements of the bus start transmitting simultaneously, the telegram with higher priority will be sent first).

KNX telegram (v2) - program the following parameters related to setting the value of KNX communication object:

Module INT-KNX - INT-KNX-2 module in which the value is to be set.

Macro Command - name of the Virtual (macro) type object, defined in INT-KNX-2 module.

Data type - size and meaning of the communication object data defined in INT-KNX-2 module for selected object.

Value - value to be set (if the type of data provides for sending a sequence of characters, you can enter up to 13 characters).

Exit delay clearing (no additional parameters to configure).

Quick arm - select the arming mode which is to be activated.

Notes:

The partitions must be controlled by user code.

The zones must not have the Bypass disabled option enabled.

The outputs must be the 24. MONO Switch, 25. BI Switch, 105. Shutter up, 106. Shutter down or Remote switch type (they need not be assigned to any group of outputs).

The keypad can be used to control the KNX system, if the INT-KNX or INT-KNX-2 module is connected to the control panel.

###### Buttons

Read - click to read the macro command related data from the keypad.

Write - click to write the macro command related data to the keypad.

Quit - click to cancel reading or writing the macro command related data.

Reset - click to restore keypad factory settings (after the factory settings have been restored, click on Read, to read data from the keypad).

Defining the macro commands

##### Defining the macro commands

- Click on the Read button to read the macro command related data from the keypad.

- Click the Definitions tab.

- Click the New macro button. A new macro command will appear in the list.

- Enter a name for the new macro command.

- If the macro command name is to be displayed on the keypad, enable the Show name option.

- If the macro command is to be run without entering the code by the user, enter the code with a suitable authority level.

- If running the macro command is to be each time preceded by user authorization, enable the Authorization required option.

- If the macro command is not to be available, when any of the partitions operated by the keypad is armed, enable the Disabled if armed option.

- If the macro command is to be run instantly on tapping the icon of macro command group, enable the Autoexecute option (if so, only this single macro command is to be assigned to the group).

- If the confirmation messages are not to be displayed after running the macro command, enable the No confirmation messages option.

- Select the icon which will be used to present the macro command on the keypad.

- If the icon is to change depending on the selected output state:

- enable the State follow output option;

- indicate the output number;

- select the icons which will illustrate inactive and active status of the output.

- Click on the  button in the Command field and select from the list the function the new macro command is to execute.

- Configure the command parameters as required.

- Click the Add button. A new command will appear in the list of commands assigned to the macro command. After clicking the command you can still make a correction of its parameters. After making the changes, click the Change button.

- Repeat the steps 13-15, if you want to add next commands.

- Click the Groups tab.

- Click the group to be edited.

- Enter the group name, if it is to be displayed on the keypad.

- Select the icon which will be used to present the group of macro commands on the keypad.

- Enable the Macro available on the status screen option for the group, if macro commands assigned to the group are to be displayed after touching a corner of the status screen.

- Enable the Icon visible on the status screen option for the group, if the group icon is to be displayed in a corner of the status screen.

- Click the Add macro button. A list of all defined macro commands will be displayed.

- Click on a macro command to add it to the group. The macro command will be put in the tree under the group.

- Click on the Write button to write the macro command related data to the keypad.

##### Status screen

Before making any changes, click on the Read button, and after making the changes - on the Write button. The status screen related data are stored in the keypad and are not read / written when you click on the  /  button in the main menu.

Note: If the Icon visible on the status screen option is enabled for a group of macro commands, do not place any elements in the screen corner where the icon will be displayed, or they will be covered by the icon. The DLOADX program indicates using appropriate graphic symbols the screen corners where the icons will be displayed.

The status screen is displayed automatically after the keypad is idle for 60 seconds. This rule does not apply if the terminal is running. In such a case, the status screen may be displayed later or even will not be displayed at all (e.g. when the service menu is open). The following information can be displayed on the status screen:

any text,

partition status by means of symbols (select individual partitions whose status will be displayed),

zone status by means of symbols (select individual zones whose status will be displayed),

output status by means of symbols (select individual outputs whose status will be displayed),

temperature (indicate the control panel zone to which the temperature detector is assigned, and define whether the temperature is to be displayed in Celsius or Fahrenheit degrees),

date and time (particular elements, such as day, month, year, hour, minutes and seconds are to be configured individually),

keypad name,

zone status by means of messages (select individual zones whose status will be displayed, and define the content and color of messages for normal state and for violation, because only these two states are presented in the form of message),

output status by means of messages (select individual outputs whose status will be displayed, and define the content and color of messages for active and inactive output).

There are three font sizes available for use on the status screen. You can also define color of the font to be used. Using the “drag and drop” method, you can easily select the place where the given information will be presented on the display.

Change picture every - the parameter defines how quickly the pictures will change during the slide show. The slide show can be displayed as the status screen background or the screensaver. The photos to be displayed should be stored on a microSD memory. Their size should not exceed 800 x 480 pixels. Only images in BMP format are supported. If the programmed time is 0, the pictures will not change (the first picture stored on the microSD card will be displayed all the time).

Show clock - if this option is enabled, the clock and status bar will be displayed after the keypad is idle for 10 minutes.

Color - you can select the color of the clock.

###### Buttons

- click to move the selected element up in the list.

- click to move the selected element down in the list.

Add - click to place on the status screen the information selected in the field above.

Delete - click to remove from the status screen the selected information.

Wallpaper - click to select another status screen wallpaper.

Save to SD card - click to save the new wallpaper on the microSD card.

Export to file - click to export the status screen settings to a file.

Import from file - click to import the status screen settings from a file.

Read - click to read the data from the keypad.

Write - click to write the data to the keypad.

Quit - click to terminate data reading/writing.

#### INT-TSI

INT-TSI - hardwired touchscreen keypad.

The keypad enables the control panel to be operated and programmed.

-----------------------------------------------------------

Name - individual name of the keypad (up to 16 characters).

Note: In the case of the keypad working in SLAVE mode, the name can only be edited in the TSI Builder program.

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

CHIME signal of zones - the numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - zone violation will not trigger the CHIME signal,

orange - zone violation will trigger the CHIME signal.

Double-click on the field to change its color.

If the zone is armed, violation will not trigger the CHIME signal.

Zone disabling chime - zone, which, if violated, will disable the CHIME feature for specified time.

Note: The zone 256 cannot disable the CHIME feature.

Bypass time - time during which the CHIME signal will be disabled after violation of the zone which disables the signaling (time is counted from the zone restore). If the value 0 is programmed, the signaling will not be disabled.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, the fire alarm can be triggered from the keypad by using the widget or terminal (tapping and holding  key for about 3 seconds).

PANIC - if this option is enabled, the panic alarm can be triggered from the keypad by using the widget or terminal (tapping and holding  key for about 3 seconds).

AUX. - if this option is enabled, the medical (auxiliary) alarm can be triggered from the keypad by using the widget or terminal (tapping and holding  key for about 3 seconds).

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Sign. alarms - with this option enabled, the keypad will signal the alarms audibly.

Key sounds - when this option is enabled, tapping the keypad screen is confirmed by beeps.

Sign. trbl. in part. arm - if this option is enabled, the troubles are not indicated after all operated from the keypad partitions are armed (if the option is disabled, the troubles are not indicated after just one of the partitions is armed).

Sign. new trouble - with this option enabled, the keypad can audibly signal the occurrence of a new trouble (if the Trouble memory until review option is enabled). New trouble signaling is cleared after the troubles have been reviewed by the user.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened by means of:

- the widget (macro command reducing the exit delay time);

- the terminal (after tapping in turn the  and  keys).

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Show disarm messages - if this option is enabled, the keypad will inform about disarming with a displayed message at all times. If the option is disabled - only in case of disarming from the given keypad.

Show arm messages - if this option is enabled, the keypad will inform about arming with a displayed message (irrespective of how the system was armed).

INT-TSI SLAVE - option for the keypad working in MASTER mode. If the option is enabled, the control panel supports the keypad working in SLAVE mode, which communicates via the keypad working in MASTER mode.

Quick control - if this option is enabled the user can:

- use the zone control widgets in the template available without login,

- start the Control user function from the terminal after tapping in turn the  and  keys (without entering the code).

###### Zones

For each of the keypad zones can be defined whether it will be used or not.

Tamper signaled in part. - partition where alarm will be triggered in the event of keypad tamper, triggering the alarm from keypad etc.

Power supply source - you can define the source from which the keypad is powered: control panel mainboard, expander with power supply or other power source. If you select the control panel mainboard or expander with power supply, the keypad backlight intensity will be reduced to approx. 15% in case of loss of AC power supply of the control panel or expander.

###### Buttons

Copy - click to open Copy window.

State inspections

User functions definition

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled:

- the user can check the state of zones on the terminal by long pressing the key with number 1 for about 3 seconds;

- the widget presenting the state of zones will always indicate the status of all zones (the widget can be used in the template available without login).

4 - partitions armed - if this option is enabled:

- the user can check the state of partitions on the terminal by long pressing the key with number 4 for about 3 seconds;

- the widget presenting the state of partitions will always indicate the status of all partitions (the widget can be used in the template available without login)..

5 - alarm events memory - if this option is enabled, the user can view the alarms log on the terminal by long pressing the key with number 5 for about 3 seconds.

6 - trouble memory - if this option is enabled, the user can view the troubles log on the terminal by long pressing the key with number 6 for about 3 seconds

7 - trouble status - if this option is enabled:

- the user can view the current troubles on the terminal by long pressing the key with number 7 for about 3 seconds;

- the widget presenting the troubles can be used in the template available without login.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by means of the terminal, long pressing the key with number 8 for about 3 seconds.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the terminal.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the terminal.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and tapping the selected arrow key on the terminal.

#### ETHM-1

The following Ethernet modules are identified as the ETHM-1:

ETHM-1 Plus

ETHM-1

Ethernet communication module enables:

reporting events via the Ethernet network,

sending event notifications using e-mail messages,

operating the alarm system from mobile devices,

programming the control panel via the Ethernet network.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

###### Network settings

Obtain IP address automatically (DHCP) - if this option is enabled, the module will automatically download data on IP address, subnet mask and gateway from the DHCP server (in such a case, you do not have to program these parameters).

IP address - module IP address.

Subnet mask - the mask of the subnet in which the module is working.

Gateway - IP address of the network device through which the other devices in the local network can communicate with devices in other networks.

Obtain DNS server address automatically - if this option is enabled, the DNS server IP address is downloaded automatically from the DHCP server. The option is available, when the Obtain IP address automatically (DHCP) option is enabled.

DNS server - IP address of the DNS server which is to be used by the module. It can be programmed, if the Obtain DNS server address automatically option is disabled.

###### DLOADX

Communication with DLOADX - if this option is enabled, connection can be established between the DLOADX program and the alarm control panel via the module.

Port - number of the TCP port used for communication with the DLOADX program. You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7090.

DLOADX key - a string of up to 12 alphanumeric characters (digits, letters and special characters) used for data encryption during communication with the DLOADX program via module.

DLOADX server - address of the computer running the DLOADX program. If the computer is not in the same local network, it must be a public address. You can enter either the IP address or the domain name.

Port - number of the TCP port used for communication with the DLOADX program. You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7090.

###### GUARDX/INTEGRA CONTROL

GUARDX - if this option is enabled, connection can be established between the GUARDX program and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

WWW - if this option is enabled, connection can be established between the web browser and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

GSM conn. - if this option is enabled, connection can be established between the INTEGRA CONTROL application and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

INTEGRUM (client) - if this option is enabled, connection can be established between the INTEGRUM system (version 2.0 or newer) and the alarm control panel via the module. When the option is enabled, the GUARDX, WWW and GSM conn. options are not available.

Port - number of the TCP port used for communication with:

- GUARDX program,

- JAVA application in the web browser,

- INTEGRA CONTROL application in the mobile device.

You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7091.

WWW port - number of the TCP port used for communication with the web browser. You can enter values from 1 do 65535 The value must be different from that entered for the other ports. Default value: 80.

GUARDX server - address of the computer running the GUARDX program or INTEGRUM server. If the computer is not used in the same local network, it must be a public address. For the computer with GUARDX program, you can enter the IP address or domain name. For the INTEGRUM system server, enter the domain name (e.g. integrum.ip.com).

GUARDX/Java key - a string of up to 12 alphanumeric characters (digits, letters and special characters) used for data encryption during communication between the control panel and:

- GUARDX program,

- JAVA application in the web browser,

- INTEGRA CONTROL application in the mobile device,

- INTEGRUM system.

GUARDX server - address of the computer running the GUARDX program. If the computer is not used in the same local network, it must be a public address. You can enter either the IP address or the domain name.

WWW port - number of the TCP port used for communication with the web browser. You can enter values from 1 do 65535 The value must be different from that entered for the other ports. Default value: 80.

Port - number of the TCP port used for communication with:

- GUARDX program,

- JAVA application in the web browser,

- INTEGRA CONTROL application in the mobile device,

- INTEGRUM system.

You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7091.

###### Wrong login

Log event - if this option is enabled, all unauthorized attempts to connect to the module are written to the event log.

Alarm - if this option is enabled, any unauthorized attempt to connect to the module will trigger the tamper alarm. The option is available if the Log event option is enabled.

###### Integration

Integration - if this option is enabled, the module can be used for integration of the alarm control panel with other systems.

Encrypted integration - if this option is enabled, communication with other systems is encrypted (see also Keypad bus).

Port - number of the TCP port used for integration. You can enter values from 1 do 65535. The value must be different from that entered for the other ports. Default value: 7094.

###### PING test

PING test - if this option is enabled, the module can perform a communication test using the ping command sent to the indicated network device. (see also Keypad bus).

###### SATEL server

Connection via Satel server - if the option is enabled, the module connects to the SATEL server and the communication via the SATEL server with the control panel can be established (Connection Setup Service). This way of communication requires no additional configuring of the network device through which the module connects to the public network.

Notes:

If two or more communication modules (ETHM-1 Plus / INT-GSM) are connected to the control panel, the Connection via Satel server option is to be enabled in one of them only. Otherwise, communication with the SATEL server will only be established with the module having the lowest address.

For establishing communication with the SATEL server, the DNS server must be used.

For communication via the SATEL server, the ports of 1024-65535 range are used as outgoing ports. These ports must not be blocked.

Push notifications - if this option is enabled, the INTEGRA CONTROL application can provide information about alarm system events by means of push notifications.

###### Integration

Integration - if this option is enabled, the module can be used for integration of the alarm control panel with other systems.

Encrypted integration - if this option is enabled, communication with other systems is encrypted (see also Keypad bus).

Port - number of the TCP port used for integration. You can enter values from 1 do 65535. The value must be different from that entered for the other ports. Default value: 7094.

###### Wrong login

Log event - if this option is enabled, all unauthorized attempts to connect to the module are written to the event log.

Alarm - if this option is enabled, any unauthorized attempt to connect to the module will trigger the tamper alarm. The option is available, if the Log event option is enabled.

###### Information

MAC - module hardware address.

ID - individual ID number assigned to the module by the SATEL server.

IP - local address / public address of the module.

QR-code - click the button to open the window in which the QR code is displayed. The QR code contains information required when configuring settings of communication through the SATEL server. You can read the QR code by using a mobile device or export to the file and transmit to the users. The QR code facilitates configuring the INTEGRA CONTROL application settings.

Refresh - click to refresh all information.

LAN uplink loss report delay - if the Ethernet network is not available for a preset period of time, the module will report a trouble. A delay in reporting the trouble prevents sending information about short-time loss of Ethernet connectivity.

IP filter

User functions definition

GUARDX/INTEGRA CONTROL

##### IP filter

Using IP filtering allows you to enhance security level of the alarm system. Establishing connection with the alarm control panel via ETHM-1 Plus module will only be possible from defined IP addresses or subnets. IP filtering does not apply to communication with the SATEL server.

You can configure IP filtering for the incoming connections:

from DLOADX program,

from GUARDX program (applies also to web browser, mobile application and INTEGRUM system),

as part of integration.

In each case you can define the filtering rules in one of the following configurations:

up to 4 allowed IP addresses,

1 allowed subnet and up to 2 allowed IP addresses,

up to 2 allowed subnets.

Note: To activate the filtering feature, enter a value in one of the four fields available for the given type of incoming connections.

IP Address - if the subnet option is disabled: the network address from which connection with the Ethernet module can be established. If the subnet option is enabled: the IP address used for defining the subnet from which connection with the Ethernet module can be established.

subnet - if the option is enabled, you can define the subnet from which incoming connections will be received by the module.

Subnet mask - mask used for separating the portion defining subnet from the IP address.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key. The settings apply to the virtual keypad in GUARDX program, web browser and mobile application.

#### INT-GSM

INT-GSM - GPRS communication module.

GPRS communication module enables:

GPRS and SMS reporting,

SMS and e-mail messaging,

SMS and CLIP control,

operating the alarm system from mobile devices,

configuring the alarm control panel via GPRS.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

###### INT-GSM options

SIM 1 / SIM 2 - if this option is enabled, the given SIM card is supported by the INT-GSM module. Disable the option if the given card is not to be used. Disabling the option will prevent unnecessary reporting of troubles related to that card.

SMS messaging - if this option is enabled, the INT-GSM module can send notifications about alarm system events in the form of SMS messages.

###### DLOADX

Communication with DLOADX - if this option is enabled, connection can be established between the DLOADX program and the alarm control panel via the module.

DLOADX key - a string of up to 12 alphanumeric characters (digits, letters and special characters) used for data encryption during communication with the DLOADX program via module.

DLOADX server - address of the computer with DLOADX program. If the computer is not in the same local network, it must be a public address. You can enter either the IP address or the domain name.

Port - number of the TCP port used for communication with the DLOADX program. You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7090.

###### GUARDX/INTEGRA CONTROL

GUARDX - if this option is enabled, connection can be established between the GUARDX program and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

INTEGRA CONTROL - if this option is enabled, connection can be established between the INTEGRA CONTROL application and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

INTEGRUM (client) - if this option is enabled, connection can be established between the INTEGRUM system (version 2.0 or newer) and the alarm control panel via the module. When the option is enabled, the GUARDX and INTEGRA CONTROL options are not available.

GUARDX server - address of the computer with GUARDX program or the INTEGRUM server. If the computer is not part of the same local network, it must be a public address. For the computer with GUARDX program, you can enter the IP address or domain name. For the INTEGRUM system server, enter the domain name (e.g. integrum.ip.com).

GUARDX key - a string of up to 12 alphanumeric characters (digits, letters and special characters) used for data encryption during communication with:

- GUARDX program,

- INTEGRA CONTROL application,

- INTEGRUM system.

Port - number of the TCP port used for communication with:

- GUARDX program,

- INTEGRA CONTROL application,

- INTEGRUM system.

You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7091.

###### SATEL server

Connection via Satel server - if the option is enabled, the module connects to the SATEL server and the communication via the SATEL server with the control panel can be established (Connection Setup Service). This way of communication requires no additional configuring of the network device through which the module connects to the public network.

Notes:

If two or more communication modules (ETHM-1 Plus / INT-GSM) are connected to the control panel, the Connection via Satel server option is to be enabled in one of them only. Otherwise, communication with the SATEL server will only be established with the module having the lowest address.

For establishing communication with the SATEL server, the DNS server must be used.

For communication via the SATEL server, the ports of 1024-65535 range are used as outgoing ports. These ports must not be blocked.

Push notifications - if this option is enabled, the INTEGRA CONTROL application can provide information about alarm system events by means of push notifications.

###### Information

IMEI - individual identification number of the GSM telephone.

ID - individual ID number assigned to the INT-GSM module by the SATEL server.

QR-code - click the button to open the window in which the QR code is displayed. The QR code contains information required when configuring settings of communication through the SATEL server. You can read the QR code by using a mobile device or export to the file and transmit to the users. The QR code facilitates configuring the INTEGRA CONTROL application settings.

[GSM signal] - information about GSM signal strength and GSM network operator.

Refresh - click to refresh all information.

INT-GSM functions

User functions definition

GUARDX/INTEGRA CONTROL

##### INT-GSM functions

GSM phone

Pre-paid support

SMS messaging / CLIP control

SMS control

Reporting

Remote firmware update

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### GSM phone

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

###### SIM 1 / SIM 2

PIN - PIN code of the SIM card.

Note: If an incorrectly programmed PIN code is used, the module will report a trouble. After the third attempt to use a wrong PIN code, the SIM card will be blocked. To unblock the SIM card, remove it and insert into a mobile phone. Then, enter the PUK code.

GPRS APN - access point name for Internet GPRS connection.

Username - user name for Internet GPRS connection.

Password - password for Internet GPRS connection.

DNS server - IP address of DNS server to be used by the module. If the address has been saved by the operator to the SIM card memory, you do not have to program it. Otherwise, it is recommended that you program the IP address of the DNS server. The IP address is necessary for sending data using GPRS technology if the address of the device the module is to connect to (monitoring station, computer with DLODX or GUARDX program, INTEGRUM server) is entered as a name.

Note: The GPRS parameters can be obtained from the GSM network operator.

MCC/MNC code - codes of the operator of GSM network to which the SIM card is to log in. Enter in turn:

- MCC (Mobile Country Code) - country code,

- MNC (Mobile Network Code) - operator code.

Remember that entering invalid data may make logging into the GSM network impossible. Unless you enter the code, the module will log into the available GSM network.

auto - if this option is enabled and the module cannot log into the network of GSM operator defined by means of the MCC/MNC code, it will log into the available GSM network.

SMS center number - telephone number of the short message service center. It is used as a connecting link when sending SMS messages. If the number has been saved by the operator to the SIM card memory, it need not be programmed. Otherwise, if the module is to send SMS messages, it must be entered. The number must be suitable for the operator of network in which the SIM card is registered.

Lock time - the time during which switch-over to the other SIM card is impossible. The time is counted from the moment of switch-over to the given card. For reporting, the transmission paths programmed as subsequent ones, if they require switch-over to the other card, will be skipped during the lock time countdown. Entering the value 0 means that instant switch-over to the other SIM card is possible.

Return time - the time after which the other SIM card is to be used. Entering the value 0 means that automatic switch-over to the other SIM card will not take place.

Note: If two SIM cards are to be used, one of them must be treated as the priority card. It is recommended that return time equal to 0 be programmed for it.

SMS for sending USSD code - control command that will be sent in the SMS message together with USSD code. The control panel will run the USSD code and send the response received from the operator to the phone number from which the SMS message with control command was sent. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Notes:

The command content must be different from that of the other control commands.

The SMS message with the USSD code must look like this: xxxxxx=yyyy= (“xxxxxx” - control command, “yyyy” - USSD code supported by the GSM network operator).

It is not advisable to use the advanced functions available due to the USSD service if menu is presented in response to the entered code.

The control command for sending USSD codes can be used for sending SMS messages through the control panel.

USSD codes from any number - if this option is enabled, the control command for sending the USSD codes or checking the SIM card balance can be sent from any telephone. If the option is disabled, the command can only be sent from the telephone whose number is stored in the module (SMS messaging / CLIP control).

Time from GSM network - if this option is enabled, the control panel clock can be synchronized with the time of the GSM network operator.

###### SMS

SMS initiating DLOADX connection - the control command which, if sent in the SMS message, will initiate communication between the alarm control panel and the DLOADX program via the module. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

SMS initiating GUARDX connection - the control command which, if sent in the SMS message, will initiate connection between the alarm control panel and the GUARDX program via the module. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Notes:

The content of control commands must vary.

The content of one control command must not be inserted into the content of another command.

You can include in the SMS message the address of computer the module is to connect to, and the number of TCP port to be used for communication. Such a message should look like this: xxxx=aaaa:p= (“xxxx” - control command; “aaaa” - address of the computer (IP address or domain name); “p” - port number).

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### Pre-paid support

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

###### SIM 1 / SIM 2

USSD-check balance - the USSD code which is used to check balance of the SIM card account. If the code has been programmed, the module can check the SIM card account balance.

Minimum level - the minimum amount of funds on the SIM card account. If the amount of funds drops below the minimum level:

- trouble will be reported,

- where the SIM card account balance is checked automatically, information on the account balance will be sent as an SMS message to the telephones for SMS messaging / CLIP control, for which the SMS>> option is enabled (SMS messaging / CLIP control).

Entering 0 will disable the checking.

Check balance SMS - the control command which, if sent in the SMS message, will run the function of checking the SIM card balance. The module will execute the USSD code programmed in the USSD-check balance field and will send the reply obtained from the operator to the telephone number from which the control command was received. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Note: If the PUSH notifications option is enabled in the module, notification of the balance of the SIM card account on which there are no funds to send an SMS message, but there are funds for the Internet service will be sent as a push message (INTEGRA CONTROL app must be installed on the phone).

Check balance at - the hour at which the module will check the SIM card account balance. If you enter no value, the checking will be disabled.

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### SMS messaging / CLIP control

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

You can program 16 telephone numbers to which notifications of alarm system events can be sent by the module. The content of SMS messages is generated automatically, based on descriptions from the control panel event log.

If a user of the alarm control panel is assigned to a telephone number, the control panel can be operated from that telephone by using CLIP and SMS messages.

Additionally, you can indicate a control panel user that will be able to operate the control panel from any telephone number (Txx). It is advisable to create a control panel user with authority level suited for the SMS/CLIP control, not for everyday operation of the alarm system.

The module can send notifications of events by SMS if the SMS messaging option is enabled in the module settings.

Telephone no. - telephone number to which SMS notifications will be sent by the module.

User - user of the alarm control panel. If you define a user for the given number (including any telephone number - line Txx), it will be possible to operate the alarm control panel from that number by using CLIP and SMS messages (SMS control). Enter the user number or click on the  button to select a user from the list. The user must have rights to run a function by using CLIP/SMS.

Note: The download of new firmware and/or update of module firmware can be initiate by using SMS message from the telephone number for which the user has been defined (Remote firmware update).

###### SMS messaging

ON - define whether the given telephone is to be notified:

X - yes,

blank field - no.

Double-click on the field to make changes.

Partitions - define of which events occurring in which partitions the given telephone number is to be notified. Click on  to open the window that allows the list of partitions to be edited. The numbers of fields in the table correspond to the partition numbers. Double-click on a field to select it (orange color) or deselect it (white color). Having finished editing, click on the OK button. If you select no partition, the number will not be notified of any events.

Events type - define whether the given telephone is to be notified of events of the given type:

X - yes,

blank field - no.

Double-click on the field to make changes.

###### CLIP control

CLIP means calling without establishing connection (you must hang up on hearing the ring signal), i.e. toll-free. The module will identify the phone number of the calling party and respond accordingly.

In the lines T1 to T16, you can program a function to be run by using CLIP from the telephone whose number has been programmed in this line. In the line Txx, you can program a function to be run by using CLIP from any telephone number.

Using the CLIP control is possible if the control panel user who is authorized to run the given function has been selected in the User column.

Note: The telephone numbers programmed in the lines from T1 to T16 are not treated by the module as any numbers.

Function - the function to be run by CLIP. Enter the function number or click on the  button to select the function from the list. The list of available functions is defined in the SMS control tab.

###### Forward SMS

SMS>> - if this option is enabled, unknown SMS messages received by the module are forwarded to the phone number (e.g. information received from the GSM network operator).

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### SMS control

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

The module enables the users to control the alarm system by using SMS messages containing appropriate control commands. The SMS messages must be sent to the SIM card number. You can program 32 control commands in the module.

Control SMS - the control command which, if sent in the SMS message, will run in the control panel the function selected in the Function field. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Notes:

The content of control commands must vary.

The content of one control command must not be inserted into the content of another command.

Several control commands may be included in one SMS message (should be separated by spaces).

The control command may be just a fragment of the SMS message. This makes it is possible to write the control command, including the comments, to the telephone memory and send the whole to the module.

Function - function run by the control command received in the SMS message or by CLIP. Enter the function number or click on the  button to select the function from the list:

1: State (text)

2: State (symb.)

3: Arm (0) - full arming.

4: Arm (1) - full arming + bypasses.

5: Arm (2) - arming without interior.

6: Arm (3) - arming without interior and without entry delay.

7: Disarm

8: Clear alarm

9: Outputs ON

10: Outputs OFF

11: Switch state

12: Bypass zones

13: Isolate zones

14: Unbypass zones

15: Trigger zone

Notes:

The partitions must be controlled by user code.

The zones that are to be bypassed, must not have the Bypass disabled option enabled.

The outputs must be the 24. MONO Switch, 25. BI Switch, 105. Shutter up, 106. Shutter down or Remote switch type.

Parameters - define the parameters the given function will be run with. Click on  to open the window that allows you to edit the list of parameters. The numbers of the table fields correspond to those of partitions / outputs / zones. Double-click on a field to select it (orange color) or deselect it (white color). For the function 15: Trigger zone, you can only select one zone. Having finished editing, click OK.

Any no. - if this option is enabled, the given function can be run from any telephone number. The control panel can be controlled from any telephone number if the alarm control panel user has been selected for any telephone number in the SMS messaging / CLIP control tab.

Par. in SMS - if this option is enabled, the given function can be run with parameters sent together with the control command in the SMS message. This makes it possible to run the function with other parameters than those programmed for it in the Parameters field. If this is the case, the SMS message must look like this: xxxxxx=a,b,c,d= (“xxxxxx” - control command, “a,b,c,d” - parameters, e.g. 1,2,3,4 (numbers of partitions / outputs / zones separated with commas)). For the 15: Trigger zone function, the control command must have the following form: xxxxxx=a= (“xxxxxx” - control command, “a” - zone number, e.g. 1 (you can indicate only one zone)).

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### Reporting

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

The module enables the alarm control panel to send event codes to the monitoring station using the following transmission paths:

GPRS,

SMS messages (no acknowledgement of event code receipt).

###### Station 1 / Station 2

Transmission priority

If sending an event code to the monitoring station using one transmission path fails, the module can use another transmission path. You must specify the order of using different transmission paths by the module. A successful send of the event code to the monitoring station will terminate the procedure (except for the test transmissions).

Notes:

The module will only use the transmission paths for which priority is specified (they are included in the list defining the order of using transmission paths).

In the case of SMS reporting, the module gets no acknowledgement of receiving the event codes by the monitoring station, hence this transmission path should be used as the last one.

The switch-over from one SIM card to the other one requires time (for example, to log onto the network), so it is better to use up all the transmission paths available for one SIM card.

The switch-over from one SIM card to the other is affected by the Lock time and Return time (GSM phone).

SMS reporting

Tel. Number - phone number of the monitoring station for SMS reporting.

SMS format - SMS format for SMS reporting. It must be defined as required by the monitoring station. The SMS message format, preset by default in the module, corresponds to the default settings of the STAM-2 monitoring station (firmware version 1.2.0 or newer) for the Contact ID format.

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### Remote firmware update

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

Remote update of the INT-GSM module firmware is made possible by the UpServ update server, which is included in the SATEL product portfolio.

Update server - address of the UpServ update server. You can enter the IP address or domain name.

Port - number of the TCP port used for communication with the UpServ update server. You can enter values from 0 to 65535 (0=disabled).

Update server address in SMS - if this option is enabled, you can enter server address and port number in the SMS message initiating the firmware download from the update server. If this option is enabled and the message contains no address or port number, the module will use the preprogrammed settings.

Note: SMS messages which initiate download of new firmware and/or update of module firmware can only be sent from the telephone whose number is saved in the module (SMS messaging / CLIP control).

###### Firmware download

Note: When downloading new firmware, the module performs its normal functions.

SMS initiating download - the control command which, if sent in the SMS message, will start downloading of the new firmware from the server. You can enter up to 8 alphanumeric characters (digits, letters and special characters).

Notes:

The command content must be different from that of the other control commands preprogrammed in the control panel.

If the Update server address in SMS option is enabled and you want the module to connect to an update server other than that indicated in the module settings, the message should look like this: xxxx=aaaa:p= (“xxxx” - control command; “aaaa” - server address (IP address or domain name); “p” - port number).

The module sends out an SMS notification on how the new firmware download has proceeded. The notification is sent to the telephone from which the SMS message initiating the firmware download was received.

If an SMS message containing the firmware download initiating command is re-sent when the new firmware downloading is in progress, the module will indicate in reply the download progress (percentage value).

###### Firmware remote update

Notes:

During update of its firmware, the module does not perform its normal functions.

Before updating the module firmware, enter the Service mode in the alarm control panel. Otherwise, starting the update will make the control panel report that the INT-GSM module is not available.

SMS initiating update - the control command which, if sent in the SMS message, will start the firmware update. You can enter up to 8 alphanumeric characters (digits, letters and special characters).

Notes:

The command content must be different from that of the other control commands preprogrammed in the control panel.

The module sends out an SMS notification on how the firmware update has proceeded. The notification is sent to the telephone from which the SMS message initiating the firmware download was received.

###### Buttons

Read - click to read the settings from the module.

Write - click to write the settings to the module.

Quit - click to cancel reading or writing the settings.

Reset - click to restore module factory settings.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key. The settings apply to the virtual keypad in GUARDX program and INTEGRA CONTROL application.

#### ETHM+GSM

The ETHM-1 Plus (ETHM-1) module to which the INT-GSM (INT-GSM) module is connected is identified as ETHM+GSM. In this configuration, GPRS is used as a backup communication path and dual path reporting is possible.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

###### Network settings

Obtain IP address automatically (DHCP) - if this option is enabled, the module will automatically download data on IP address, subnet mask and gateway from the DHCP server (in such a case, you do not have to program these parameters).

IP address - module IP address.

Subnet mask - the mask of the subnet in which the module is working.

Gateway - IP address of the network device through which the other devices in the local network can communicate with devices in other networks.

Obtain DNS server address automatically - if this option is enabled, the DNS server IP address is downloaded automatically from the DHCP server. The option is available, when the Obtain IP address automatically (DHCP) option is enabled.

DNS server - IP address of the DNS server which is to be used by the module. It can be programmed if the Obtain DNS server address automatically option is disabled.

###### INT-GSM options

SIM 1 / SIM 2 - if this option is enabled, the given SIM card is supported by the INT-GSM module. Disable the option if the given card is not to be used. Disabling the option will prevent unnecessary reporting of troubles related to that card.

SMS messaging - if this option is enabled, the INT-GSM module can send notifications about alarm system events in the form of SMS messages.

###### DLOADX

Communication with DLOADX - if this option is enabled, connection can be established between the DLOADX program and the alarm control panel via the module.

DLOADX key - a string of up to 12 alphanumeric characters (digits, letters and special characters) used for data encryption during communication with the DLOADX program via module.

DLOADX server - address of the computer running the DLOADX program. If the computer is not in the same local network, it must be a public address. You can enter either the IP address or the domain name.

Port - number of the TCP port used for communication with the DLOADX program. You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7090.

###### GUARDX/INTEGRA CONTROL

GUARDX - if this option is enabled, connection can be established between the GUARDX program and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

WWW - if this option is enabled, connection can be established between the web browser and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

GSM conn. - if this option is enabled, connection can be established between the INTEGRA CONTROL application and the alarm control panel via the module. The option is not available when the INTEGRUM (client) option is enabled.

INTEGRUM (client) - if this option is enabled, connection can be established between the INTEGRUM system (version 2.0 or newer) and the alarm control panel via the module. When the option is enabled, the GUARDX, WWW and GSM conn. options are not available.

GUARDX server - address of the computer running the GUARDX program or INTEGRUM server. If the computer is not used in the same local network, it must be a public address. For the computer with GUARDX program, you can enter the IP address or domain name. For the INTEGRUM system server, enter the domain name (e.g. integrum.ip.com).

GUARDX key - a string of up to 12 alphanumeric characters (digits, letters and special characters) used for data encryption during communication between the control panel and:

- GUARDX program,

- JAVA application in the web browser,

- INTEGRA CONTROL application in the mobile device,

- INTEGRUM system.

WWW port - number of the TCP port used for communication with the web browser. You can enter values from 1 do 65535 The value must be different from that entered for the other ports. Default value: 80.

Port - number of the TCP port used for communication with:

- GUARDX program,

- JAVA application in the web browser,

- INTEGRA CONTROL application in the mobile device,

- INTEGRUM system.

You can enter values from 1 to 65535. The value must be different from that entered for the other ports. Default value: 7091.

###### PING test

PING test - if this option is enabled, the module can perform a communication test using the ping command sent to the indicated network device. (see also Keypad bus).

###### SATEL server

Connection via Satel server - if the option is enabled, the module connects to the SATEL server and the communication via the SATEL server with the control panel can be established (Connection Setup Service). This way of communication requires no additional configuring of the network device through which the module connects to the public network.

Notes:

If two or more communication modules (ETHM-1 Plus / INT-GSM) are connected to the control panel, the Connection via Satel server option is to be enabled in one of them only. Otherwise, communication with the SATEL server will only be established with the module having the lowest address.

For establishing communication with the SATEL server, the DNS server must be used.

For communication via the SATEL server, the ports of 1024-65535 range are used as outgoing ports. These ports must not be blocked.

Push notifications - if this option is enabled, the INTEGRA CONTROL application can provide information about alarm system events by means of push notifications.

###### Integration

Integration - if this option is enabled, the module can be used for integration of the alarm control panel with other systems.

Encrypted integration - if this option is enabled, communication with other systems is encrypted (see also Keypad bus).

Port - number of the TCP port used for integration. You can enter values from 1 do 65535. The value must be different from that entered for the other ports. Default value: 7094.

###### Wrong login

Log event - if this option is enabled, all unauthorized attempts to connect to the module are written to the event log.

Alarm - if this option is enabled, any unauthorized attempt to connect to the module will trigger the tamper alarm. The option is available if the Log event option is enabled.

###### Information

MAC - module hardware address.

ID - individual ID number assigned to the module by the SATEL server.

IP - local address / public address of the module.

[GSM signal] - information about GSM signal strength and GSM network operator.

QR-code - click the button to open the window in which the QR code is displayed. The QR code contains information required when configuring settings of communication through the SATEL server. You can read the QR code by using a mobile device or export to the file and transmit to the users. The QR code facilitates configuring the INTEGRA CONTROL application settings.

Refresh - click to refresh all information.

LAN uplink loss report delay - if the Ethernet network is not available for a preset period of time, the module will report a trouble. A delay in reporting the trouble prevents sending information about short-time loss of Ethernet connectivity.

INT-GSM functions

IP filter

User functions definition

GUARDX/INTEGRA CONTROL

##### INT-GSM functions

GSM phone

Pre-paid support

SMS messaging / CLIP control

SMS control

Reporting

Remote firmware update

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### GSM phone

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

###### SIM 1 / SIM 2

PIN - PIN code of the SIM card.

Note: If an incorrectly programmed PIN code is used, the module will report a trouble. After the third attempt to use a wrong PIN code, the SIM card will be blocked. To unblock the SIM card, remove it and insert into a mobile phone. Then, enter the PUK code.

GPRS APN - access point name for Internet GPRS connection.

Username - user name for Internet GPRS connection.

Password - password for Internet GPRS connection.

DNS server - IP address of DNS server to be used by the module. If the address has been saved by the operator to the SIM card memory, you do not have to program it. Otherwise, it is recommended that you program the IP address of the DNS server. The IP address is necessary for sending data using GPRS technology if the address of the device the module is to connect to (monitoring station, computer with DLODX or GUARDX program, INTEGRUM server) is entered as a name.

Note: The GPRS parameters can be obtained from the GSM network operator.

MCC/MNC code - codes of the operator of GSM network to which the SIM card is to log in. Enter in turn:

- MCC (Mobile Country Code) - country code,

- MNC (Mobile Network Code) - operator code.

Remember that entering invalid data may make logging into the GSM network impossible. Unless you enter the code, the module will log into the available GSM network.

auto - if this option is enabled and the module cannot log into the network of GSM operator defined by means of the MCC/MNC code, it will log into the available GSM network.

SMS center number - telephone number of the short message service center. It is used as a connecting link when sending SMS messages. If the number has been saved by the operator to the SIM card memory, it need not be programmed. Otherwise, if the module is to send SMS messages, it must be entered. The number must be suitable for the operator of network in which the SIM card is registered.

Lock time - the time during which switch-over to the other SIM card is impossible. The time is counted from the moment of switch-over to the given card. For reporting, the transmission paths programmed as subsequent ones, if they require switch-over to the other card, will be skipped during the lock time countdown. Entering the value 0 means that instant switch-over to the other SIM card is possible.

Return time - the time after which the other SIM card is to be used. Entering the value 0 means that automatic switch-over to the other SIM card will not take place.

Note: If two SIM cards are to be used, one of them must be treated as the priority card. It is recommended that return time equal to 0 be programmed for it.

SMS for sending USSD code - control command that will be sent in the SMS message together with USSD code. The control panel will run the USSD code and send the response received from the operator to the phone number from which the SMS message with control command was sent. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Notes:

The command content must be different from that of the other control commands.

The SMS message with the USSD code must look like this: xxxxxx=yyyy= (“xxxxxx” - control command, “yyyy” - USSD code supported by the GSM network operator).

It is not advisable to use the advanced functions available due to the USSD service if menu is presented in response to the entered code.

The control command for sending USSD codes can be used for sending SMS messages through the control panel.

USSD codes from any number - if this option is enabled, the control command for sending the USSD codes or checking the SIM card balance can be sent from any telephone. If the option is disabled, the command can only be sent from the telephone whose number is stored in the module (SMS messaging / CLIP control).

Time from GSM network - if this option is enabled, the control panel clock can be synchronized with the time of the GSM network operator.

Do not report LAN trouble if INT-GSM connected to SATEL server - if this option is enabled, loss of the Ethernet network will not be reported, when connection has been successfully established with the SATEL server via the INT-GSM module (GPRS).

Do not report LAN trouble if INT-GSM connected to SMTP server - if this option is enabled, loss of the Ethernet network will not be reported, when connection has been successfully established with the SMTP server via the INT-GSM module (GPRS).

Do not report LAN trouble if INT-GSM connected to NTP server - if this option is enabled, loss of the Ethernet network will not be reported, when connection has been successfully established with the NTP server via the INT-GSM module (GPRS).

###### SMS

SMS initiating DLOADX connection - the control command which, if sent in the SMS message, will initiate communication between the alarm control panel and the DLOADX program via ETHM-1 Plus module. If connection cannot be established over Ethernet, an attempt will be made to establish communication via INT-GSM module (GPRS). You can enter up to 16 alphanumeric characters (digits, letters and special characters).

SMS initiating GUARDX connection - the control command which, if sent in the SMS message, will initiate connection between the alarm control panel and the GUARDX program via ETHM-1 Plus module. If connection cannot be established over Ethernet, an attempt will be made to establish communication via INT-GSM module (GPRS). You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Notes:

The content of control commands must vary.

The content of one control command must not be inserted into the content of another command.

You can include in the SMS message the address of computer the module is to connect to, and the number of TCP port to be used for communication. Such a message should look like this: xxxx=aaaa:p= (“xxxx” - control command; “aaaa” - address of the computer (IP address or domain name); “p” - port number).

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### Pre-paid support

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

###### SIM 1 / SIM 2

USSD-check balance - the USSD code which is used to check balance of the SIM card account. If the code has been programmed, the module can check the SIM card account balance.

Minimum level - the minimum amount of funds on the SIM card account. If the amount of funds drops below the minimum level:

- trouble will be reported,

- where the SIM card account balance is checked automatically, information on the account balance will be sent as an SMS message to the telephones for SMS messaging / CLIP control, for which the SMS>> option is enabled (SMS messaging / CLIP control).

Entering 0 will disable the checking.

Check balance SMS - the control command which, if sent in the SMS message, will run the function of checking the SIM card balance. The module will execute the USSD code programmed in the USSD-check balance field and will send the reply obtained from the operator to the telephone number from which the control command was received. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Note: If the PUSH notifications option is enabled in the module, notification of the balance of the SIM card account on which there are no funds to send an SMS message, but there are funds for the Internet service will be sent as a push message (INTEGRA CONTROL app must be installed on the phone).

Check balance at - the hour at which the module will check the SIM card account balance. If you enter no value, the checking will be disabled.

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### SMS messaging / CLIP control

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

You can program 16 telephone numbers to which notifications of alarm system events can be sent by the module. The content of SMS messages is generated automatically, based on descriptions from the control panel event log.

If a user of the alarm control panel is assigned to a telephone number, the control panel can be operated from that telephone by using CLIP and SMS messages.

Additionally, you can indicate a control panel user that will be able to operate the control panel from any telephone number (Txx). It is advisable to create a control panel user with authority level suited for the SMS/CLIP control, not for everyday operation of the alarm system.

The module can send notifications of events by SMS if the SMS messaging option is enabled in the module settings.

Telephone no. - telephone number to which SMS notifications will be sent by the module.

User - user of the alarm control panel. If you define a user for the given number (including any telephone number - line Txx), it will be possible to operate the alarm control panel from that number by using CLIP and SMS messages (SMS control). Enter the user number or click on the  button to select a user from the list. The user must have rights to run a function by using CLIP/SMS.

Note: The download of new firmware and/or update of INT-GSM module firmware can be initiate by using SMS message from the telephone number for which the user has been defined (Remote firmware update).

###### SMS messaging

ON - define whether the given telephone is to be notified:

X - yes,

blank field - no.

Double-click on the field to make changes.

Partitions - define of which events occurring in which partitions the given telephone number is to be notified. Click on  to open the window that allows the list of partitions to be edited. The numbers of fields in the table correspond to the partition numbers. Double-click on a field to select it (orange color) or deselect it (white color). Having finished editing, click on the OK button. If you select no partition, the number will not be notified of any events.

Events type - define whether the given telephone is to be notified of events of the given type:

X - yes,

blank field - no.

Double-click on the field to make changes.

###### CLIP control

CLIP means calling without establishing connection (you must hang up on hearing the ring signal), i.e. toll-free. The module will identify the phone number of the calling party and respond accordingly.

In the lines T1 to T16, you can program a function to be run by using CLIP from the telephone whose number has been programmed in this line. In the line Txx, you can program a function to be run by using CLIP from any telephone number.

Using the CLIP control is possible if the control panel user who is authorized to run the given function has been selected in the User column.

Note: The telephone numbers programmed in the lines from T1 to T16 are not treated by the module as any numbers.

Function - the function to be run by CLIP. Enter the function number or click on the  button to select the function from the list. The list of available functions is defined in the SMS control tab.

###### Forward SMS

SMS>> - if this option is enabled, unknown SMS messages received by the module are forwarded to the phone number (e.g. information received from the GSM network operator).

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### SMS control

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

The module enables the users to control the alarm system by using SMS messages containing appropriate control commands. The SMS messages must be sent to the SIM card number. You can program 32 control commands in the module.

Control SMS - the control command which, if sent in the SMS message, will run in the control panel the function selected in the Function field. You can enter up to 16 alphanumeric characters (digits, letters and special characters).

Notes:

The content of control commands must vary.

The content of one control command must not be inserted into the content of another command.

Several control commands may be included in one SMS message (should be separated by spaces).

The control command may be just a fragment of the SMS message. This makes it is possible to write the control command, including the comments, to the telephone memory and send the whole to the module.

Function - function run by the control command received in the SMS message or by CLIP. Enter the function number or click on the  button to select the function from the list:

1: State (text)

2: State (symb.)

3: Arm (0) - full arming.

4: Arm (1) - full arming + bypasses.

5: Arm (2) - arming without interior.

6: Arm (3) - arming without interior and without entry delay.

7: Disarm

8: Clear alarm

9: Outputs ON

10: Outputs OFF

11: Switch state

12: Bypass zones

13: Isolate zones

14: Unbypass zones

15: Trigger zone

Notes:

The partitions must be controlled by user code.

The zones that are to be bypassed, must not have the Bypass disabled option enabled.

The outputs must be the 24. MONO Switch, 25. BI Switch, 105. Shutter up, 106. Shutter down or Remote switch type.

Parameters - define the parameters the given function will be run with. Click on  to open the window that allows you to edit the list of parameters. The numbers of the table fields correspond to those of partitions / outputs / zones. Double-click on a field to select it (orange color) or deselect it (white color). For the function 15: Trigger zone, you can only select one zone. Having finished editing, click OK.

Any no. - if this option is enabled, the given function can be run from any telephone number. The control panel can be controlled from any telephone number if the alarm control panel user has been selected for any telephone number in the SMS messaging / CLIP control tab.

Par. in SMS - if this option is enabled, the given function can be run with parameters sent together with the control command in the SMS message. This makes it possible to run the function with other parameters than those programmed for it in the Parameters field. If this is the case, the SMS message must look like this: xxxxxx=a,b,c,d= (“xxxxxx” - control command, “a,b,c,d” - parameters, e.g. 1,2,3,4 (numbers of partitions / outputs / zones separated with commas)). For the 15: Trigger zone function, the control command must have the following form: xxxxxx=a= (“xxxxxx” - control command, “a” - zone number, e.g. 1 (you can indicate only one zone)).

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### Reporting

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

The modules enable the alarm control panel to send event codes to the monitoring station using the following transmission paths:

Ethernet,

GPRS,

SMS messages (no acknowledgement of event code receipt).

###### Station 1 / Station 2

Transmission priority

If sending an event code to the monitoring station using one transmission path fails, the module can use another transmission path. You must specify the order of using different transmission paths by the module. A successful send of the event code to the monitoring station will terminate the procedure (except for the test transmissions).

Notes:

The module will only use the transmission paths for which priority is specified (they are included in the list defining the order of using transmission paths).

In the case of dual path reporting program:

- just one transmission path for Station 1: ETHM (Ethernet),

- priority transmission path for Station 2: GPRS SIM1 or GPRS SIM 2.

In the case of SMS reporting, the module gets no acknowledgement of receiving the event codes by the monitoring station, hence this transmission path should be used as the last one.

The switch-over from one SIM card to the other one requires time (for example, to log onto the network), so it is better to use up all the transmission paths available for one SIM card.

The switch-over from one SIM card to the other is affected by the Lock time and Return time (GSM phone).

SMS reporting

Tel. Number - phone number of the monitoring station for SMS reporting.

SMS format - SMS format for SMS reporting. It must be defined as required by the monitoring station. The SMS message format, preset by default in the module, corresponds to the default settings of the STAM-2 monitoring station (firmware version 1.2.0 or newer) for the Contact ID format.

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### Remote firmware update

Before making any changes, click on the Read button, and after making the changes - on the Write button. The settings displayed in the tab are not read / written when you click on the  /  button in the main menu.

Remote update of the INT-GSM module firmware is made possible by the UpServ update server, which is included in the SATEL product portfolio.

Update server - address of the UpServ update server. You can enter the IP address or domain name.

Port - number of the TCP port used for communication with the UpServ update server. You can enter values from 0 to 65535 (0=disabled).

Update server address in SMS - if this option is enabled, you can enter server address and port number in the SMS message initiating the firmware download from the update server. If this option is enabled and the message contains no address or port number, the module will use the preprogrammed settings.

Note: SMS messages which initiate download of new firmware and/or update of module firmware can only be sent from the telephone whose number is saved in the module (SMS messaging / CLIP control).

###### Firmware download

Note: When downloading new firmware, the module performs its normal functions.

SMS initiating download - the control command which, if sent in the SMS message, will start downloading of the new firmware from the server. You can enter up to 8 alphanumeric characters (digits, letters and special characters).

Notes:

The command content must be different from that of the other control commands preprogrammed in the control panel.

If the Update server address in SMS option is enabled and you want the module to connect to an update server other than that indicated in the module settings, the message should look like this: xxxx=aaaa:p= (“xxxx” - control command; “aaaa” - server address (IP address or domain name); “p” - port number).

The module sends out an SMS notification on how the new firmware download has proceeded. The notification is sent to the telephone from which the SMS message initiating the firmware download was received.

If an SMS message containing the firmware download initiating command is re-sent when the new firmware downloading is in progress, the module will indicate in reply the download progress (percentage value).

###### Firmware remote update

Notes:

During update of its firmware, the module does not perform its normal functions.

Before updating the module firmware, enter the Service mode in the alarm control panel. Otherwise, starting the update will make the control panel report that the INT-GSM module is not available.

SMS initiating update - the control command which, if sent in the SMS message, will start the firmware update. You can enter up to 8 alphanumeric characters (digits, letters and special characters).

Notes:

The command content must be different from that of the other control commands preprogrammed in the control panel.

The module sends out an SMS notification on how the firmware update has proceeded. The notification is sent to the telephone from which the SMS message initiating the firmware download was received.

###### Buttons

Read - click to read the settings from the modules.

Write - click to write the settings to the modules.

Quit - click to cancel reading or writing the settings.

Reset - click to restore INT-GSM module factory settings.

##### IP filter

Using IP filtering allows you to enhance security level of the alarm system. Establishing connection with the alarm control panel via ETHM-1 Plus module will only be possible from defined IP addresses or subnets. IP filtering does not apply to communication with the SATEL server.

You can configure IP filtering for the incoming connections:

from DLOADX program,

from GUARDX program (applies also to web browser, mobile application and INTEGRUM system),

as part of integration.

In each case you can define the filtering rules in one of the following configurations:

up to 4 allowed IP addresses,

1 allowed subnet and up to 2 allowed IP addresses,

up to 2 allowed subnets.

Note: To activate the filtering feature, enter a value in one of the four fields available for the given type of incoming connections.

IP Address - if the subnet option is disabled: the network address from which connection with the Ethernet module can be established. If the subnet option is enabled: the IP address used for defining the subnet from which connection with the Ethernet module can be established.

subnet - if the option is enabled, you can define the subnet from which incoming connections will be received by the module.

Subnet mask - mask used for separating the portion defining subnet from the IP address.

##### User functions definition

Code+arrows - you can define which functions will be started on entering the code and pressing the selected arrow key. The settings apply to the virtual keypad in GUARDX program, web browser and mobile application.

#### CA-64 PTSA

CA-64 PTSA - mimic board.

The mimic board enables visualization of the status of the alarm system partitions and zones.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Zones state / Partitions armed / Alarms in partitions - you can define how the LEDs are to indicate particular states. The way of LED operation is presented graphically for a two-second period:

gray field - the LED is off,

orange field - the LED is on.

Double-click on the field to change its color.

AC loss report delay - the time during which the device must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the device.

Communication RS - if this option is enabled, it is possible to connect a computer with GUARDX program to the keypad RS-232 port. When the option is enabled, the GUARDX on RS-232 branch will appear on the tree representing hardware.

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

Show - selection of the information to be conveyed by the LEDs.

#### INT-RS

INT-RS Plus / INT-RS - interface for systems integration.

Interface for systems integration converts data being sent through the keypad bus into the RS-232 serial bus standard. It can be used for the following applications:

connection of computer with GUARDX program installed (in much the same way as to LCD keypad),

event reporting by means of specialized external third-party modules,

operating the alarm control panel by means of software other than that offered by SATEL (capability of integrating with third-party systems).

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

#### GUARDX on RS-232

The settings described below apply to the virtual keypad in GUARDX program, when the computer running the GUARDX program is connected to the RS-232 port on LCD keypad.

The virtual keypad allows you to operate and program the alarm system in the same way as when using the physical keypad.

-----------------------------------------------------------

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

Tamper signaled in part. - partition where alarm will be triggered in the event of triggering the alarm from keypad etc.

State inspections

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

#### GUARDX/INTEGRA CONTROL

The ETHM-1 Plus / ETHM-1 / INT-GSM module enables communication to be established with the control panel by using e.g. the GUARDX program, web browser and INTEGRA CONTROL application. The settings described below apply to the virtual keypad available in the GUARDX program, web browser and INTEGRA CONTROL application after establishing connection with the control panel via this module.

The virtual keypad allows you to operate and program the alarm system in the same way as when using the physical keypad.

-----------------------------------------------------------

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Exit delay clearing enable - with this option enabled, the exit delay time in partitions with the Exit delay clearing option enabled can be shortened after pressing in turn the 9# keys.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

Tamper signaled in part. - partition where alarm will be triggered in the event of triggering the alarm from keypad etc.

State inspections

Macro Commands

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

##### Macro Commands

The tab allows you to configure macro commands which will be available in the INTEGRA CONTROL application connecting to the control panel via Ethernet module.

Before making any changes, click on the Read button, and after making the changes - on the Write button. The macro command related data are stored in the Ethernet module and are not read / written when you click on the  /  button in the main menu.

###### Groups

The macro commands which are to be available for the mobile application users must be assigned to one of the four groups. Up to 16 macro commands can be assigned to a group. The groups of macro commands and macro commands assigned to them are presented in a tree form.

Name - name of the macro command group (up to 16 characters in two lines, up to 8 characters in the line). Do not enter the name if it is not to be displayed.

Icon - icon of a group of macro commands. Click  to display the list of available icons.

Add macro - the button is available after you click on a group of macro commands. It displays a list containing the names of defined macro commands. After you click on a name, the macro command will be added to the group.

Remove macro - the button is available after you click on any macro command. It removes that macro command from the group.

- click to move the highlighted macro command down within the group.

- click to move the highlighted macro command up within the group.

Export to file - click to export defined macro commands to a file.

Import from file - click to import macro commands from a file.

###### Definitions

The macro command is a sequence of actions, composed of single commands, which are to be done by the control panel when running the macro command.

New macro - click to create a new macro command.

Remove macro - click to delete selected macro command.

Name - individual name of the macro command (up to 16 characters in two lines, up to 8 characters in the line).

Code - the code which is to be used for authorization when executing commands contained in the macro command. For execution of such commands to be possible, the code must be granted a suitable authority level. It is presented as a string of asterisks.

Note: If, when running a macro command, it turns out that the code is invalid (e.g. it has been changed in the meantime), the user will be able to enter the correct code. It will be automatically saved to the device memory (replacing the invalid one).

Authorization required - if this option is enabled, the macro command will only be run after user additional authorization.

Disabled if armed - if this option is enabled, the macro command will not be available, when any of the partitions operated by the mobile application is armed.

Autoexecute - if this option is enabled, there is no need to enter the group to run the macro command.

No confirmation messages - if this option is enabled, no messages will appear to inform the user about execution of a command or an error after running a macro command (the screen from which the macro command was run will still be displayed).

Icon

Icon - the macro command icon. The list of available icons will be displayed after you click the  button. If the State follow output option is enabled, select 2 icons for the macro commands. One icon will be displayed when the output is inactive, and the other - when the output is active.

State follow output - if this option is enabled, the icon of macro command will change depending on the status of output whose number should be selected in the field on the right side. Select an output, the status of which depends on the actions taken by the control panel after running the macro command. Thus it will be possible to inform the user by means of macro command icons about, for example, the status of outputs controlled by using macro commands or the status of partitions which are armed by a macro command.

Show name - if this option is enabled, the macro command name will be displayed.

Commands

Commands list - commands assigned to the currently highlighted macro command. The  and  buttons allow you to change the order of commands (moving the selected command up and down).

Add - click to add to the list a new command, selected in the Command field.

Change - click to save the changes to the command parameters which were made after adding the command to the list (otherwise, the changes made will not be saved).

Delete - click to remove the highlighted command from the list.

Command - the control panel executed function which can be assigned to the macro command. The list of all available functions will be displayed after you click the  button. Depending on which function you choose:

Arming - select the partitions which are to be armed (double-click on the field designated by the partition number) and define the arming mode (next clicks on the field designated by the partition number; the digit inside the field has the following meaning: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay).

Disarming - select the partitions which are to be disarmed (double-click on the field designated by the partition number).

Alarm clearing - select the partitions in which alarm is to be cleared (double-click on the field designated by the partition number).

Bypass zones - select the zones which are to be inhibited (double-click on the field designated by the zone number).

Unbypass zones - select the zones which are to be unbypassed (double-click on the field designated by the zone number).

Outputs ON - select the outputs which are to be activated (double-click on the field designated by the output number).

Outputs OFF - select the outputs which are to be deactivated (double-click on the field designated by the output number).

Change outputs state - select the outputs whose status is to be changed (double-click on the field designated by the output number).

KNX telegram - program the following parameters of KNX telegram for the INT-KNX module:

INT-KNX module - INT-KNX module which is to send the telegram.

Group address - the group address which will be inserted in the telegram.

Type - the telegram type.

Value - the value that will be inserted in the telegram (parameter available for some types of the telegram).

Priority - telegram priority (if two elements of the bus start transmitting simultaneously, the telegram with higher priority will be sent first).

KNX telegram (v2) - program the following parameters related to setting the value of KNX communication object:

Module INT-KNX - INT-KNX-2 module in which the value is to be set.

Macro Command - name of the Virtual (macro) type object, defined in INT-KNX-2 module.

Data type - size and meaning of the communication object data defined in INT-KNX-2 module for selected object.

Value - value to be set (if the type of data provides for sending a sequence of characters, you can enter up to 13 characters).

Exit delay clearing (no additional parameters to configure).

Quick arm - select the arming mode which is to be activated.

Notes:

The partitions must be controlled by user code.

The zones must not have the Bypass disabled option enabled.

The outputs must be the 24. MONO Switch, 25. BI Switch, 105. Shutter up, 106. Shutter down or Remote switch type (they need not be assigned to any group of outputs).

The mobile application can be used to control the KNX system, if the INT-KNX or INT-KNX-2 module is connected to the control panel.

###### Buttons

Read - click to read the macro command related data from the module.

Write - click to write the macro command related data to the module.

Quit - click to cancel reading or writing the macro command related data.

Reset - click to restore factory settings i.e. delete all macro commands (after the factory settings have been restored, click on Read, to read data from the module).

Defining the macro commands

##### Defining the macro commands

- Click on the Read button to read the macro command related data from the module.

- Click the Definitions tab.

- Click the New macro button. A new macro command will appear in the list.

- Enter a name for the new macro command.

- If the macro command is to be run without entering the code by the user, enter the code with a suitable authority level.

- If running the macro command is to be each time preceded by user authorization, enable the Authorization required option.

- If the macro command is not to be available, when any of the partitions operated by the mobile application is armed, enable the Disabled if armed option.

- If the macro command is to be available without entering the group, enable the Autoexecute option.

- If the confirmation messages are not to be displayed after running the macro command, enable the No confirmation messages option.

- Click the  button and select the icon for the macro command.

- If the icon is to change depending on the selected output state:

- enable the State follow output option;

- indicate the output number;

- select the icons.

- If the macro command name is to be displayed, enable the Show name option.

- Click on the  button in the Command field and select from the list the function the new macro command is to execute.

- Configure the command parameters as required.

- Click the Add button. A new command will appear in the list of commands assigned to the macro command. After clicking the command you can still make a correction of its parameters. After making the changes, click the Change button.

- Repeat the steps 12-14 if you want to add next commands.

- Click the Groups tab.

- Click the group to be edited.

- Enter the group name.

- Click the  button and select the icon for the macro command group.

- Click the Add macro button. A list of all defined macro commands will be displayed.

- Click on a macro command to add it to the group. The macro command will be put in the tree under the group.

- Click on the Write button to write the macro command related data to the module.

#### DLOADX (RS-232)

The settings described below apply to the virtual keypad in DLOADX program, when connection with the control panel has been established via the RS-232 port, external modem or ETHM-1 Plus / ETHM-1 / INT-GSM module.

The virtual keypad allows you to operate and program the alarm system in the same way as when using the physical keypad.

-----------------------------------------------------------

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

Quick Arm partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partitions will not be armed in case of the quick arming from the keypad,

orange - the partitions will be armed in case of the quick arming from the keypad.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Show viol. zones - with this option enabled, violating the CHIME signal triggering zone result additionally in the zone name being displayed.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

Tamper signaled in part. - partition where alarm will be triggered in the event of triggering the alarm from keypad etc.

State inspections

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

#### DLOADX (modem)

The settings described below refer to the virtual keypad in DLOADX program, when communication with the control panel has been established via the built-in modem.

The virtual keypad allows you to operate and program the alarm system in the same way as when using the physical keypad.

-----------------------------------------------------------

Partitions managed by keypad - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition is not operated,

orange - the partition is operated (the partition can be armed/disarmed or alarm in the partition may be cancelled from the keypad).

Double-click on the field to change its color.

Note: Using the service code you can operate all partitions, irrespective of which partitions are operated by the keypad.

Show alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate burglary alarms in the partition,

orange - the keypad indicates burglary alarms in the partition.

Double-click on the field to change its color.

Show fire alarms of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not indicate fire alarms in the partition,

orange - the keypad indicates fire alarms in the partition.

Double-click on the field to change its color.

Display entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on entry delay countdown in the partition is not displayed on the keypad,

orange - information on entry delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Display exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - information on exit delay countdown in the partition is not displayed on the keypad,

orange - information on exit delay countdown in the partition is displayed on the keypad.

Double-click on the field to change its color.

Signal entry delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the entry delay period in the partition,

orange - the keypad beeps during the entry delay period in the partition.

Double-click on the field to change its color.

Signal exit delay of partitions - the numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the keypad does not beep during the exit delay period in the partition,

orange - the keypad beeps during the exit delay period in the partition.

Double-click on the field to change its color.

Date/Time format - the format in which the date and time are to be displayed on the keypad.

###### Alarm messages

Partitions - if this option is enabled, messages on partition alarms will be displayed (they contain the name of partition).

Zones - if this option is enabled, messages on alarms from zones will be displayed (they contain the name of zone). The zone alarm messages have the priority.

###### Alarms

FIRE - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the fire alarm.

PANIC - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the panic alarm.

AUX. - if this option is enabled, pressing the  key for approx. 3 seconds will trigger the medical alarm.

3 wrong codes - if this option is enabled, entering incorrect code three times will trigger the alarm.

###### Additional options

Silent PANIC alarm - if this option is enabled, the panic alarm triggered from the keypad will be a silent one (without loud signal).

Key sounds - with this option enabled, pressing the keypad keys is confirmed by beeps.

Auto-Arm delay countdown - with this option enabled, the auto-arm delay countdown in partition is signaled acoustically.

Quick control - if this option is enabled, the Outs control user function can be started by pressing in turn the 8# keys (without the need to enter the user code).

Tamper signaled in part. - partition where alarm will be triggered in the event of triggering the alarm from keypad etc.

State inspections

##### State inspections

###### Key hold-down

Some functions can be run by the users without having to enter the code.

1 - zone state - if this option is enabled, the user can inspect the zone state after pressing and holding for 3 seconds the key with number 1.

4 - partitions armed - if this option is enabled, the user can inspect the partition state after pressing and holding for 3 seconds the key with number 4.

5 - alarm events memory - if this option is enabled, the user can view the alarms log after pressing and holding for 3 seconds the key with number 5.

6 - trouble memory - if this option is enabled, the user can view the troubles log after pressing and holding for 3 seconds the key with number 6.

7 - trouble status - if this option is enabled, the user can view the current troubles after pressing and holding for 3 seconds the key with number 7.

8 - chime on/off - if this option is enabled, the user can switch on/off the CHIME signal in the keypad by pressing and holding for 3 seconds the key with number 8.

###### Zone state

You can define the symbols which will be used to illustrate the state of zones on the display.

###### Partition state

You can define the symbols which will be used to illustrate the state of partitions on the display.

#### Copy

Copy keypad data to - select the keypad to which you want to copy the data.

Settings - if this field is selected, the settings stored in the control panel memory will be copied (the settings for macro commands and screen status are stored in the keypad memory).

Macro Commands - if this field is selected, the macro commands will be copied.

Status screen - if this field is selected, the screen status settings will be copied.

Note: The macro commands and screen status settings can only be copied to a keypad of the same type.

### Expansion modules bus

Bus short-circuit - Triggers alarm in partition - if this option is enabled, short-circuit in the bus will trigger tamper alarm in the partition you have selected in the field on the right.

Tamper alarm - Always loud signaling - if this option is enabled, a tamper alarm will be always signaled at outputs (if this option is disabled - only if system is armed).

###### Buttons

Exp. modules identification - click to start the function of identification of devices connected to the expansion modules bus (see: Identification).

Exp. modules order - click to open Exp. modules order window.

Add - click to open Add module window (the button will be available after you click on the branch representing a bus).

Delete - click to remove the selected device (the button will be available for devices added in the Add module window, provided that the changes have not been written to the control panel).

INT-CR / INT-IT

INT-S

INT-SCR

INT-ENT

INT-SZ

CA-64 SR

CA-64 DR

INT-RX

CA-64 E

CA-64 Ei / INT-E

CA-64 EPS

CA-64 EPSi / INT-EPS

INT-ADR

CA-64 ADR / INT-ADRPS

CA-64 O / INT-O

CA-64 OPS / INT-OPS

INT-ORS

INT-ORSPS

INT-IORS

INT-IORSPS

INT-PP

INT-PPPS

ACU-100

INT-VG

CA-64 SM

INT-KNX

INT-KNX-2

INT-AV

#### INT-CR/IT

INT-INT / INT-IT-2 / INT-CR - proximity card arm/disarm device.

Proximity card arm/disarm device enables arming / disarming and alarm clearing in many partitions by means of proximity cards, key fobs and other 125 kHz passive transponders.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Tamper signaled in part. - the partition in which tamper alarm will be triggered in the event of disconnection of the device from the control panel.

###### The table defining module functionality

R - reaction of the partition after moving the card away, when the red LED is on:

X - will be armed in mode “full”,

blank field - no reaction.

G - reaction of the partition after moving the card away, when the green LED (mode A) is on:

1 - will be armed in mode “full”,

2 - will be armed in mode “without interior”,

3 - will be armed in mode “without interior and without entry delay”,

blank field - no reaction.

Y - reaction of the partition after moving the card away, when the yellow LED (mode B) is on:

1 - will be armed in mode “full”,

2 - will be armed in mode “without interior”,

3 - will be armed in mode “without interior and without entry delay”,

blank field - no reaction.

Double-click on the field to make changes.

###### Options

Sign. card (hardware) - the device can signal by a single beep that the card code has been read out or the LED has lit up (the code is sent to the control panel after removal of the card and only then the panel reaction to the read code is audibly signaled).

Alarm signal - if this option is enabled, the device can audibly signal alarms during the Global alarm time.

until canceled - if this option is enabled, the device can audibly signal the alarm memory.

Sign. entry delay - if this option is enabled, the device can audibly signal the entry delay countdown.

Sign. exit delay - if this option is enabled, the device can audibly signal the exit delay countdown.

Auto-arm delay countdown - if this option is enabled, the device can audibly signal the auto-arming delay countdown.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Alarm 3 wrong cards - if this option is enabled, reading the unknown card three times will trigger an alarm.

Second code wait sign. - if this option is enabled, the device can signal by means of LEDs that it is waiting for the second card. This is a global option i.e. if enabled in any device, it will be enabled in all of them.

###### Buttons

Users - click to open Users of module window.

#### INT-S

The following devices are identified as the INT-S:

INT-S - partition keypad,

INT-SK - partition keypad,

INT-SCR - multifunctional keypad working as partition keypad.

The partition keypad allows to operate one partition in the alarm system and provides access control features.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Partition - partition operated by the keypad.

Lock - if this option is enabled, the partition keypad supports the access control functions (you can program the following parameters: Lock features, Relay ON time, Relay, Max. door open time etc.).

Lock features - relay operating mode:

ON if partition armed - relay is active when the partition is armed, and inactive when the partition is disarmed.

Note: If the partition is disarmed in a different way than by means of the partition keypad, the relay will only be deactivated after entering the code and pressing * key.

Fixed ON time - after entering the code and pressing * key, the relay will be active for the duration of Relay ON time.

Fixed ON time - OFF if door open - after entering the code and pressing * key, the relay will be active until the door is opened (the door status monitoring input disconnected from common ground), but not longer than for the duration of Relay ON time.

Fixed ON time - OFF if door closed - after entering the code and pressing * key, the relay will be active until the door is closed (the door status monitoring input reconnected to common ground), but not longer than for the duration of Relay ON time.

Relay ON time - the time period during which the relay can be active. You can enter from 1 to 255 seconds.

Relay - status of the deactivated relay [parameter does not apply to INT-SCR multifunctional keypad]:

NO - the relay contacts are open (they close on activating the relay).

NC - the relay contacts are closed (they open on activating the relay).

Authorization control - if this option is enabled, unauthorized opening of the door will save the event to the control panel memory.

Alarm on unauth. access - if this option is enabled, unauthorized opening of the door when the partition is armed will trigger an alarm. The option is available if the Authorization control option is enabled.

Max. door open time - the maximum period of time during which the door can be open (the door status monitoring input can be disconnected from common ground). If the door is open longer, audible alarm will be triggered in the keypad, and the event will be saved to the control panel memory. You can enter from the 0 to 255 seconds. If value 0 is programmed, the door status will not be monitored.

Dependent on door (1) / Dependent on door (2) - you may define the door that must be closed to be able to unlock the door controlled by the keypad (to activate the relay). You may define a door supervised by another expander or alarm system zone programmed as type 57 Technical - door open.

Confirmation - you can select whether and how the keypad is to communicate with the user during operation:

No - the keypad will not inform the user in any way about execution of or refusal to execute an operation.

Sound - the keypad will inform the user audibly about execution of or refusal to execute an operation.

Backlight - the keypad will inform the user by blinking key backlight about execution of or refusal to execute an operation.

Code+* do not disarm - if this option is enabled, entering the code and pressing * key will not disarm the partition.

Access if armed - if this option is enabled, entering the code and pressing * key will unlock the door controlled by the module even if the partition is armed. The option is available if the Code+* do not disarm option is enabled.

FIRE alarm - if this option is enabled, pressing and holding # (INT-S / INT-SCR) / * (INT-SK) key for 3 seconds will trigger the fire alarm.

AUX. alarm - if this option is enabled, pressing and holding 0 key for 3 seconds will trigger the medical alarm.

PANIC alarm - if this option is enabled, pressing and holding * (INT-S / INT-SCR) / # (INT-SK) key for 3 seconds will trigger the panic alarm.

silent - if this option is enabled, the panic alarm triggered from the keypad will be a silent alarm (without audible alarm signal). This option is available, if the PANIC alarm option is enabled.

Alarm 3 incorrect codes - if this option is enabled, entering a wrong code three times will trigger an alarm.

Quick arming - if this option is enabled, arming from the keypad is possible without entering the code.

Control “BI” output - if this option is enabled, the keypad accepts the “Bi” output operating type of codes.

Control “MONO” output - if this option is enabled, the keypad accepts the “Mono” output operating type of codes.

Partition blocking - if this option is enabled, entering the Blocking partition or Guard type of code will temporarily block the partition when armed (violating a zone belonging to the partition will not trigger any alarm). The time of blocking should be defined for the partition or the code (of the Blocking partition type).

Guard round control - if this option is enabled, entering the Guard type of code will be recorded as completion of a guard round.

Changing access code - if this option is enabled, the user can change own code from the keypad.

Exit delay clearing enable - if this option is enabled, the partition exit delay time will be reduced on pressing in turn the 9 and # keys (if the Exit delay clearing option is enabled for the partition).

Alarm signal - if this option is enabled, the keypad will audibly signal alarms throughout the Global alarm time.

Alarm signal (until canceled) - if this option is enabled, the keypad will audibly signal alarms until they are cleared.

Sign. entry delay - if this option is enabled, the keypad will audibly signal the entry delay countdown.

Sign. exit delay - if this option is enabled, the keypad will audibly signal the exit delay countdown.

Auto-Arm delay countdown - if this option is enabled, the keypad will audibly signal the auto-arm delay countdown.

Acc. code sign. (hardware) - if this option is enabled, the keypad will confirm with a single beep that the code has been entered. This signal is useful where a time lag occurs between entering the code and generating the audible signal after verification of the code by the control panel.

CHIME - if this option is enabled, the keypad will audibly signal violation of zones with Chime in module option enabled, belonging to the partition operated by means of the keypad.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Backlight - you can define how the keypad backlight will operate:

No - the keypad backlight will be permanently off.

Auto - the keypad backlight will go on after any key is pressed. Additionally, it can be turned on if a specific event occurs (see the Auto-backlight parameter). The keypad backlight goes on for about 40 seconds from pressing the key / occurrence of the event.

Permanent - the keypad backlight will be permanently on.

Auto-backlight - if the keypad backlight comes on automatically, you can additionally define whether and what event will turn the backlight on:

No - the keypad backlight will only go on after pressing any key.

Zone violation - the keypad backlight will additionally go on if a selected zone is violated.

Entry delay, part. - the keypad backlight will additionally go on if entry delay countdown starts in the selected partition.

Unlock door if fire - you can define whether and when the fire alarm will unlock the door controlled by the keypad (i.e. will activate the relay):

No - the door will not be unlocked in the event of fire alarm.

Part. fire alarm - the door will be unlocked in the event of fire alarm in the partition to which the keypad is assigned.

Object fire alarm - the door will be unlocked in the event of fire alarm in the object to which the keypad is assigned.

Fire alarm - the door will be unlocked in the event of fire alarm in the alarm system.

###### Buttons

Users - click to open Users of module window.

#### INT-SCR

INT-SCR - multifunctional keypad working as partition keypad with proximity card reader.

The partition keypad allows to operate one partition in the alarm system and provides access control features.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Partition - partition operated by the keypad.

Lock - if this option is enabled, the partition keypad supports the access control functions (you can program the following parameters: Lock features, Relay ON time, Relay, Max. door open time etc.).

Lock features - relay operating mode:

ON if partition armed - relay is active when the partition is armed, and inactive when the partition is disarmed.

Note: If the partition is disarmed in a different way than by means of the partition keypad, the relay will only be deactivated after entering the code and pressing * key / presenting the card.

Fixed ON time - after entering the code and pressing * key / presenting the card, the relay will be active for the duration of Relay ON time.

Fixed ON time - OFF if door open - after entering the code and pressing * key / presenting the card, the relay will be active until the door is opened (the door status monitoring input disconnected from common ground), but not longer than for the duration of Relay ON time.

Fixed ON time - OFF if door closed - after entering the code and pressing * key / presenting the card, the relay will be active until the door is closed (the door status monitoring input reconnected to common ground), but not longer than for the duration of Relay ON time.

Relay ON time - the time period during which the relay can be active. You can enter from 1 to 255 seconds.

Authorization control - if this option is enabled, unauthorized opening of the door will save the event to the control panel memory.

Alarm on unauth. access - if this option is enabled, unauthorized opening of the door when the partition is armed will trigger an alarm. The option is available if the Authorization control option is enabled.

Max. door open time - the maximum period of time during which the door can be open (the door status monitoring input can be disconnected from common ground). If the door is open longer, audible alarm will be triggered in the keypad, and the event will be saved to the control panel memory. You can enter from the 0 to 255 seconds. If value 0 is programmed, the door status will not be monitored.

Dependent on door (1) / Dependent on door (2) - you may define the door that must be closed to be able to unlock the door controlled by the keypad (to activate the relay). You may define a door supervised by another expander or alarm system zone programmed as type 57 Technical - door open.

Confirmation - you can select whether and how the keypad is to communicate with the user during operation:

No - the keypad will not inform the user in any way about execution of or refusal to execute an operation.

Sound - the keypad will inform the user audibly about execution of or refusal to execute an operation.

Backlight - the keypad will inform the user by blinking key backlight about execution of or refusal to execute an operation.

Code+* do not disarm - if this option is enabled, entering the code and pressing * key / presenting the card will not disarm the partition.

Access if armed - if this option is enabled, entering the code and pressing * key / presenting the card will unlock the door controlled by the module even if the partition is armed. The option is available, if the Code+* do not disarm option is enabled.

Code+# equal to code+* - if this option is enabled, response to entering the code and pressing the # key / holding the card is the same as to pressing the * key / presenting the card.

FIRE alarm - if this option is enabled, pressing and holding # key for 3 seconds will trigger the fire alarm.

AUX. alarm - if this option is enabled, pressing and holding 0 key for 3 seconds will trigger the medical alarm.

PANIC alarm - if this option is enabled, pressing and holding * key for 3 seconds will trigger the panic alarm.

silent - if this option is enabled, the panic alarm triggered from the keypad will be a silent alarm (without audible alarm signal). This option is available, if the PANIC alarm option is enabled.

Alarm 3 incorrect codes - if this option is enabled, entering a wrong code / reading an unknown card three times will trigger an alarm.

Quick arming - if this option is enabled, arming from the keypad is possible without entering the code.

Control “BI” output - if this option is enabled, the keypad accepts the “Bi” output operating type of codes.

Control “MONO” output - if this option is enabled, the keypad accepts the “Mono” output operating type of codes.

Partition blocking - if this option is enabled, entering the Blocking partition or Guard type of code will temporarily block the partition when armed (violating a zone belonging to the partition will not trigger any alarm). The time of blocking should be defined for the partition or the code (of the Blocking partition type).

Guard round control - if this option is enabled, entering the Guard type of code will be recorded as completion of a guard round.

Changing access code - if this option is enabled, the user can change own code from the keypad.

Exit delay clearing enable - if this option is enabled, the partition exit delay time will be reduced on pressing in turn the 9 and # keys (if the Exit delay clearing option is enabled for the partition).

Alarm signal - if this option is enabled, the keypad will audibly signal alarms throughout the Global alarm time.

Alarm signal (until canceled) - if this option is enabled, the keypad will audibly signal alarms until they are cleared.

Sign. entry delay - if this option is enabled, the keypad will audibly signal the entry delay countdown.

Sign. exit delay - if this option is enabled, the keypad will audibly signal the exit delay countdown.

Auto-Arm delay countdown - if this option is enabled, the keypad will audibly signal the auto-arm delay countdown.

Acc. code sign. (hardware) - if this option is enabled, the keypad will confirm with a single beep that the code has been entered / card has been read. This signal is useful where a time lag occurs between entering the code / reading the card and generating the audible signal after verification of the code / card by the control panel.

CHIME - if this option is enabled, the keypad will audibly signal violation of zones with Chime in module option enabled, belonging to the partition operated by means of the keypad.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Backlight - you can define how the keypad backlight will operate:

No - the keypad backlight will be permanently off.

Auto - the keypad backlight will go on after any key is pressed. Additionally, it can be turned on if a specific event occurs (see the Auto-backlight parameter). The keypad backlight goes on for about 40 seconds from pressing the key / reading the card / occurrence of the event.

Permanent - the keypad backlight will be permanently on.

Auto-backlight - if the keypad backlight comes on automatically, you can additionally define whether and what event will turn the backlight on:

No - the keypad backlight will only go on after pressing any key.

Zone violation - the keypad backlight will additionally go on if a selected zone is violated.

Entry delay, part. - the keypad backlight will additionally go on if entry delay countdown starts in the selected partition.

Unlock door if fire - you can define whether and when the fire alarm will unlock the door controlled by the keypad (i.e. will activate the relay):

No - the door will not be unlocked in the event of fire alarm.

Part. fire alarm - the door will be unlocked in the event of fire alarm in the partition to which the keypad is assigned.

Object fire alarm - the door will be unlocked in the event of fire alarm in the object to which the keypad is assigned.

Fire alarm - the door will be unlocked in the event of fire alarm in the alarm system.

###### Code+card

Code OR card - the user can use code or card for authentication.

Code AND card - the user must use code and card for authentication.

Follow output - the authentication method depends on the status of selected output (the output active - code and card; the output inactive - code or card).

###### Buttons

Users - click to open Users of module window.

#### INT-ENT

INT-ENT - multifunctional keypad working as entry keypad.

The entry keypad allows to activate the delay for the 3. Interior delayed type zones.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Partition - partition operated by the keypad.

Delay activation time - the time counted from the code entering or card reading, during which the 3. Interior delayed type zones (in the partition operated by keypad) acts as delayed ones. If the partition is not disarmed during the countdown, the interior delayed zones will again act as instant ones.

Confirmation - you can select whether and how the keypad is to communicate with the user during operation:

No - the keypad will not inform the user in any way about execution of or refusal to execute an operation.

Sound - the keypad will inform the user audibly about execution of or refusal to execute an operation.

Backlight - the keypad will inform the user by blinking key backlight about execution of or refusal to execute an operation.

Alarm 3 incorrect codes - if this option is enabled, entering a wrong code / reading an unknown card three times will trigger an alarm.

Control “BI” output - if this option is enabled, the keypad accepts the “Bi” output operating type of codes.

Control “MONO” output - if this option is enabled, the keypad accepts the “Mono” output operating type of codes.

Guard round control - if this option is enabled, entering the Guard type of code will be recorded as completion of a guard round.

Delay activation sign. - if this option is enabled, the keypad will audibly signal the countdown of delay activation time.

Acc. code sign. (hardware) - if this option is enabled, the keypad will confirm with a single beep that the code has been entered / card has been read. This signal is useful where a time lag occurs between entering the code / reading the card and generating the audible signal after verification of the code / card by the control panel.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Backlight - you can define how the keypad backlight will operate:

No - the keypad backlight will be permanently off.

Auto - the keypad backlight will go on after any key is pressed. The keypad backlight goes on for about 40 seconds from pressing the key / reading the card.

Permanent - the keypad backlight will be permanently on.

###### Buttons

Users - click to open Users of module window.

#### INT-SZ

INT-SZ / INT-SZK - code lock.

The code lock provides access control features.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Partition - partition to which the code lock belongs (alarms will be triggered in this partition).

Lock features - relay operating mode after entering the code and pressing * or # key:

Fixed ON time - the relay is active for the duration of Relay ON time.

Fixed ON time - OFF if door open - the relay is active until the door is opened (the door status monitoring input disconnected from common ground), but not longer than for the duration of Relay ON time.

Fixed ON time - OFF if door closed - the relay is active until the door is closed (the door status monitoring input reconnected to common ground), but not longer than for the duration of Relay ON time.

Relay ON time - the time period during which the relay can be active. You can enter from 1 to 255 seconds.

Relay - status of the deactivated relay:

NO - the relay contacts are open (they close on activating the relay).

NC - the relay contacts are closed (they open on activating the relay).

Authorization control - if this option is enabled, unauthorized opening of the door will save the event to the control panel memory.

Alarm on unauth. access - if this option is enabled, unauthorized opening of the door when the partition is armed will trigger an alarm. The option is available if the Authorization control option is enabled.

Max. door open time - the maximum period of time during which the door can be open (the door status monitoring input can be disconnected from common ground). If the door is open longer, audible alarm will be triggered in the code lock, and the event will be saved to the control panel memory. You can enter from the 0 to 255 seconds. If value 0 is programmed, the door status will not be monitored.

Dependent on door (1) / Dependent on door (2) - you may define the door that must be closed to be able to unlock the door controlled by the code lock (to activate the relay). You may define a door supervised by another expander or alarm system zone programmed as type 57 Technical - door open.

Confirmation - you can select whether and how the code lock is to communicate with the user during operation:

No - the code lock will not inform the user in any way about execution of or refusal to execute an operation.

Sound - the code lock will inform the user audibly about execution of or refusal to execute an operation.

Backlight - the code lock will inform the user by blinking key backlight about execution of or refusal to execute an operation.

FIRE alarm - if this option is enabled, pressing and holding # (INT-SZ) / * (INT-SZK) key for 3 seconds will trigger the fire alarm.

AUX. alarm - if this option is enabled, pressing and holding 0 key for 3 seconds will trigger the medical alarm.

PANIC alarm - if this option is enabled, pressing and holding * (INT-SZ) / # (INT-SZK) key for 3 seconds will trigger the panic alarm.

silent - if this option is enabled, the panic alarm triggered from the keypad will be a silent alarm (without audible alarm signal). This option is available, if the PANIC alarm option is enabled.

Alarm 3 incorrect codes - if this option is enabled, entering a wrong code three times will trigger an alarm.

Control “BI” output - if this option is enabled, the code lock accepts the “Bi” output operating type of codes.

Control “MONO” output - if this option is enabled, the code lock accepts the “Mono” output operating type of codes.

Partition blocking - if this option is enabled, entering the Blocking partition or Guard type of code will temporarily block the partition when armed (violating a zone belonging to the partition will not trigger any alarm). The time of blocking should be defined for the partition or the code (of the Blocking partition type).

Guard round control - if this option is enabled, entering the Guard type of code will be recorded as completion of a guard round.

Changing access code - if this option is enabled, the user can change own code from the code lock.

Acc. code sign. (hardware) - if this option is enabled, the code lock will confirm with a single beep that the code has been entered. This signal is useful where a time lag occurs between entering the code and generating the audible signal after verification of the code by the control panel.

CHIME - if this option is enabled, the code lock will audibly signal violation of zones with Chime in module option enabled, belonging to the same partition as code lock.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Backlight - you can define how the key backlight will operate:

No - OFF.

Auto - goes on automatically after any key is pressed. Additionally, it can be turned on if a specific event occurs (see the Auto-backlight parameter). The backlight goes on for about 40 seconds from pressing the key / occurrence of the event.

Permanent - ON.

Auto-backlight - if the key backlight comes on automatically, you can additionally define whether and what event will turn the backlight on:

No - the key backlight will only go on after pressing any key.

Zone violation - the key backlight will additionally go on if a selected zone is violated.

Entry delay, part. - the key backlight will additionally go on if entry delay countdown starts in the selected partition.

Unlock door if fire - you can define whether and when the fire alarm will unlock the door controlled by the code lock (i.e. will activate the relay):

No - the door will not be unlocked in the event of fire alarm.

Part. fire alarm - the door will be unlocked in the event of fire alarm in the partition to which the code lock belongs.

Object fire alarm - the door will be unlocked in the event of fire alarm in the object to which the code lock belongs.

Fire alarm - the door will be unlocked in the event of fire alarm in the alarm system.

###### Buttons

Users - click to open Users of module window.

#### CA-64 SR

The following devices are identified as the CA-64 SR:

INT-R - universal expander for card / iButton readers working as CA-64 SR expander,

CA-64 SR - expander for proximity card reader.

The expander provides access control features.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Partition - partition to which the expander belongs (alarms will be triggered in this partition).

Lock - if this option is enabled, the expander can perform access control functions. Define how the relay is to operate:

ON if partition armed - relay is active when the partition is armed, and inactive when the partition is disarmed.

Note: If the partition is disarmed in a different way than by means of the reader, the relay will only be deactivated after presenting the card.

Fixed ON time - after presenting the card, the relay will be active for the duration of Relay ON time.

Fixed ON time - OFF if door open - after presenting the card, the relay will be active until the door is opened (the door status monitoring input disconnected from common ground), but not longer than for the duration of Relay ON time.

Fixed ON time - OFF if door closed - after presenting the card, the relay will be active until the door is closed (the door status monitoring input reconnected to common ground), but not longer than for the duration of Relay ON time.

Relay ON time - the time period during which the relay can be active. You can enter from 1 to 255 seconds.

Max. door open time - the maximum period of time during which the door can be open (the door status monitoring input can be disconnected from common ground). If the door is open longer, audible alarm will be triggered in the readers, and the event will be saved to the control panel memory. You can enter from the 0 to 255 seconds. If value 0 is programmed, the door status will not be monitored.

Dependent on door (1) / Dependent on door (2) - you may define the door that must be closed to be able to unlock the door controlled by the expander (to activate the relay). You may define a door supervised by another expander or alarm system zone programmed as type 57 Technical - door open.

No auto-disarm - if this option is enabled, presenting the card to the reader will not disarm the partition. In order to disarm the partition, hold the card at the reader.

Access if armed - if this option is enabled, presenting the card will unlock the door controlled by the module even if the partition is armed. The option is available, if the No auto-disarm option is enabled.

Authorization control - if this option is enabled, unauthorized opening of the door will save the event to the control panel memory.

Alarm on unauth. access - if this option is enabled, unauthorized opening of the door when the partition is armed will trigger an alarm. The option is available if the Authorization control option is enabled.

Reader control - if this option is enabled, the expander controls the reader presence. Lack of the reader will generate a trouble The reader presence control can be effected if the reader is provided with a presence control circuit (the white wire).

Confirmation - you can define how the reader is to communicate with the user:

Sound - if this option is enabled, the reader will inform the user audibly about execution of or refusal to execute an operation.

LED - if this option is enabled, the reader will inform the user by means of LEDs about execution of or refusal to execute an operation.

Arm - if this option is enabled, the reader can be used for arming the partition.

No disarming - if this option is enabled, disarming by means of readers is impossible.

Reader tamper alarm - if this option is enabled, lack of the reader will trigger tamper alarm. The option is available, if the Reader control option is enabled for reader A or B.

Sign. card (hardware) - if this option is enabled, the readers will confirm with a single beep that the card has been read. This signal is useful where a time lag occurs between reading the card and generating the audible signal after verification of the card by the control panel.

Alarm 3 incorrect codes - if this option is enabled, reading an unknown card three times will trigger an alarm.

Control “BI” output - if this option is enabled, the expander accepts the “Bi” output operating type of codes.

Control “MONO” output - if this option is enabled, the expander accepts the “Mono” output operating type of codes.

Partition blocking - if this option is enabled, reading the card of the user who uses a code of the Blocking partition or Guard type will temporarily block the partition when armed (violating a zone belonging to the partition will not trigger any alarm). The time of blocking should be defined for the partition or the code (of the Blocking partition type).

Guard round control - if this option is enabled, reading the card of the user who uses a code of the Guard type will be recorded as completion of a guard round.

Alarm signal - if this option is enabled, the proximity card readers will audibly signal alarms throughout the Global alarm time.

until canceled - if this option is enabled, the proximity card readers will audibly signal alarms until they are cleared.

Sign. entry delay - if this option is enabled, the proximity card readers will audibly signal the entry delay countdown.

Sign. exit delay - if this option is enabled, the proximity card readers will audibly signal the exit delay countdown.

Auto-Arm delay countdown - if this option is enabled, the proximity card readers will audibly signal the auto-arm delay countdown.

CHIME - if this option is enabled, the proximity card readers will audibly signal violation of zones with Chime in module option enabled, belonging to the same partition as the expander.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Unlock door if fire - you can define whether and when the fire alarm will unlock the door controlled by the expander (i.e. will activate the relay):

No - the door will not be unlocked in the event of fire alarm.

Part. fire alarm - the door will be unlocked in the event of fire alarm in the partition to which the expander belongs.

Object fire alarm - the door will be unlocked in the event of fire alarm in the object to which the expander belongs.

Fire alarm - the door will be unlocked in the event of fire alarm in the alarm system.

###### Buttons

Users - click to open Users of module window.

#### CA-64 DR

The following devices are identified as the CA-64 DR:

INT-R - universal expander for card / iButton readers working as CA-64 DR expander,

CA-64 DR - expander for DALLAS iButton readers.

The expander provides access control features.

Note: If the DALLAS iButton readers are to communicate with the users by using sounds, connect two electric transducers to the expander (one per reader).

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Partition - partition to which the expander belongs (alarms will be triggered in this partition).

Lock - if this option is enabled, the expander can perform access control functions. Define how the relay is to operate:

ON if partition armed - relay is active when the partition is armed, and inactive when the partition is disarmed.

Note: If the partition is disarmed in a different way than by means of the reader, the relay will only be deactivated after touching the iButton to the reader.

Fixed ON time - after touching the iButton to the reader, the relay will be active for the duration of Relay ON time.

Fixed ON time - OFF if door open - after touching the iButton to the reader, the relay will be active until the door is opened (the door status monitoring input disconnected from common ground), but not longer than for the duration of Relay ON time.

Fixed ON time - OFF if door closed - after touching the iButton to the reader, the relay will be active until the door is closed (the door status monitoring input reconnected to common ground), but not longer than for the duration of Relay ON time.

Relay ON time - the time period during which the relay can be active. You can enter from 1 to 255 seconds.

Max. door open time - the maximum period of time during which the door can be open (the door status monitoring input can be disconnected from common ground). If the door is open longer, audible alarm will be triggered in the readers, and the event will be saved to the control panel memory. You can enter from the 0 to 255 seconds. If value 0 is programmed, the door status will not be monitored.

Dependent on door (1) / Dependent on door (2) - you may define the door that must be closed to be able to unlock the door controlled by the expander (to activate the relay). You may define a door supervised by another expander or alarm system zone programmed as type 57 Technical - door open.

No auto-disarm - if this option is enabled, touching the DALLAS iButton to the reader will not disarm the partition. In order to disarm the partition, hold the DALLAS iButton to the reader.

Access if armed - if this option is enabled, touching the DALLAS iButton to the reader will unlock the door controlled by the module even if the partition is armed. The option is available, if the No auto-disarm option is enabled.

Authorization control - if this option is enabled, unauthorized opening of the door will save the event to the control panel memory.

Alarm on unauth. access - if this option is enabled, unauthorized opening of the door when the partition is armed will trigger an alarm. The option is available if the Authorization control option is enabled.

Confirmation - you can define how the reader is to communicate with the user:

Sound - if this option is enabled, execution of or refusal to execute an operation is audibly signaled.

LED - if this option is enabled, the reader will inform the user by means of LEDs about execution of or refusal to execute an operation.

Arm - if this option is enabled, the reader can be used for arming the partition.

No disarming - if this option is enabled, disarming by means of readers is impossible.

Sign. card (hardware) - if this option is enabled, the iButton reading can be signaled with a single beep. This signal is useful where a time lag occurs between reading the iButton and generating the audible signal after verification of the iButton by the control panel.

Alarm 3 incorrect codes - if this option is enabled, reading an unknown iButton three times will trigger an alarm.

Control “BI” output - if this option is enabled, the expander accepts the “Bi” output operating type of codes.

Control “MONO” output - if this option is enabled, the expander accepts the “Mono” output operating type of codes.

Partition blocking - if this option is enabled, reading the iButton of the user who uses a code of the Blocking partition or Guard type will temporarily block the partition when armed (violating a zone belonging to the partition will not trigger any alarm). The time of blocking should be defined for the partition or the code (of the Blocking partition type).

Guard round control - if this option is enabled, reading the iButton of the user who uses a code of the Guard type will be recorded as completion of a guard round.

Alarm signal - if this option is enabled, the alarms are audibly signaled throughout the Global alarm time.

until canceled - if this option is enabled, the alarms are audibly signaled until they are cleared.

Sign. entry delay - if this option is enabled, the entry delay countdown is audibly signaled.

Sign. exit delay - if this option is enabled, the exit delay countdown is audibly signaled.

Auto-Arm delay countdown - if this option is enabled, the auto-arm delay countdown is audibly signaled.

CHIME - if this option is enabled, violation of zones with Chime in module option enabled, belonging to the same partition as the expander, is audibly signaled.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Unlock door if fire - you can define whether and when the fire alarm will unlock the door controlled by the expander (i.e. will activate the relay):

No - the door will not be unlocked in the event of fire alarm.

Part. fire alarm - the door will be unlocked in the event of fire alarm in the partition to which the expander belongs.

Object fire alarm - the door will be unlocked in the event of fire alarm in the object to which the expander belongs.

Fire alarm - the door will be unlocked in the event of fire alarm in the alarm system.

###### Buttons

Users - click to open Users of module window.

#### INT-RX

INT-RX / INT-RX-S - 433 MHz keyfobs receiver expansion module.

The expander enables operation of the alarm system using the 433 MHz keyfobs.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Edit keyfobs - click to open Keyfobs INT-RX window.

#### CA-64 E

CA-64 E - zone expander.

Zone expander enables the system expansion by 8 programmable hardwired zones.

-----------------------------------------------------------

The window presents information on expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

Name - individual name of the device (up to 16 characters).

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### CA-64 Ei / INT-E

CA-64 Ei / INT-E - zone expander.

Zone expander enables the system expansion by 8 programmable hardwired zones.

-----------------------------------------------------------

The window presents information on expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

Name - individual name of the device (up to 16 characters).

EOL resistance value - the value of end-of-line resistors. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

When programming the R3 resistor value, remember that it must differ from that of the R2 resistor by at least 500 Ohm.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### CA-64 EPS

CA-64 EPS - zone expander with power supply.

Zone expander enables the system expansion by 8 programmable hardwired zones.

-----------------------------------------------------------

The window presents information on expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

Name - individual name of the device (up to 16 characters).

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### CA-64 EPSi / INT-EPS

CA-64 EPSi / INT-EPS - zone expander with power supply.

Zone expander enables the system expansion by 8 programmable hardwired zones.

-----------------------------------------------------------

The window presents information on expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

Name - individual name of the device (up to 16 characters).

EOL resistance value - the value of end-of-line resistors. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

When programming the R3 resistor value, remember that it must differ from that of the R2 resistor by at least 500 Ohm.

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-ADR

INT-ADR - addressable zone expander.

The expander enables the system expansion by 48 addressable zones.

-----------------------------------------------

The window presents information on expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- address.

Name - individual name of the device (up to 16 characters).

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### CA-64 ADR / INT-ADRPS

CA-64 ADR / INT-ADRPS - addressable zone expander with power supply.

The expander enables the system expansion by 48 addressable zones.

-----------------------------------------------

The window presents information on expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- address.

Name - individual name of the device (up to 16 characters).

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### CA-64 O / INT-O

CA-64 O / INT-O - output expander.

Output expander enables the system expansion by 8 programmable hardwired outputs.

-----------------------------------------------------------

The window presents information on expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### CA-64 OPS / INT-OPS

CA-64 OPS / INT-OPS - output expander with power supply.

Output expander enables the system expansion by 8 programmable hardwired outputs.

-----------------------------------------------------------

The window presents information on expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-ORS

INT-ORS - DIN-rail output expander.

The expander enables expansion of the system by 8 programmable relay outputs. The relays are capable of controlling electrical devices supplied with 230 V AC voltage.

-----------------------------------------------------------

The window presents information on expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-ORSPS

INT-ORSPS - DIN-rail output expander with power supply.

The expander enables expansion of the system by 8 programmable relay outputs. The relays are capable of controlling electrical devices supplied with 230 V AC voltage.

-----------------------------------------------------------

The window presents information on expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-IORS

INT-IORS - DIN-rail zone/output expander.

The expander enables the system expansion by:

- 8 programmable hardwired zones,

- 8 programmable relay outputs. The relays are capable of controlling electrical devices supplied with 230 V AC voltage.

-----------------------------------------------------------

The window presents information on:

expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

EOL resistance value - the value of end-of-line resistors. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

When programming the R3 resistor value, remember that it must differ from that of the R2 resistor by at least 500 Ohm.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-IORSPS

INT-IORSPS - DIN-rail zone/output expander with power supply.

The expander enables the system expansion by:

- 8 programmable hardwired zones,

- 8 programmable relay outputs. The relays are capable of controlling electrical devices supplied with 230 V AC voltage.

-----------------------------------------------------------

The window presents information on:

expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

EOL resistance value - the value of end-of-line resistors. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

When programming the R3 resistor value, remember that it must differ from that of the R2 resistor by at least 500 Ohm.

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-PP

INT-PP - zone/output expander.

The expander enables the system expansion by:

- 8 programmable hardwired zones,

- 8 programmable hardwired outputs.

-----------------------------------------------------------

The window presents information on:

expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

EOL resistance value - the value of end-of-line resistors. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

When programming the R3 resistor value, remember that it must differ from that of the R2 resistor by at least 500 Ohm.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### INT-PPPS

CA-64 PP / INT-PPPS - zone/output expander with power supply.

The expander enables the system expansion by:

- 8 programmable hardwired zones,

- 8 programmable hardwired outputs.

-----------------------------------------------------------

The window presents information on:

expander zones:

- zone number in the system (determined during the identification),

- name,

- zone type,

- wiring type.

expander outputs:

- output number in the system (determined during the identification),

- name,

- type.

Name - individual name of the device (up to 16 characters).

EOL resistance value - the value of end-of-line resistors. You can enter values from the 500 Ohm to 15 kOhm range. The figure below shows the numbering of EOL resistors (T - tamper, A - alarm, M - masking). In case of the EOL and 2EOL configurations, the R3 resistor value is irrelevant. In case of the EOL configuration, the resistor value is a sum of the values programmed for the R1 and R2 resistors.

Notes:

The sum of preset values may not exceed 15 kOhm.

When programming the R3 resistor value, remember that it must differ from that of the R2 resistor by at least 500 Ohm.

AC loss report delay - the time during which the expander must remain without AC power for the trouble to be reported. The trouble report delay prevents reporting the short-time power failures which have no effect on normal operation of the system.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of expander tamper.

###### Buttons

Advanced - click to open the Exp. modules order window.

#### ACU-100

The following controllers of ABAX wireless system are identified as ACU-100:

ACU-120

ACU-270

ACU-100

ACU-250

The controller makes it possible to use in the alarm system:

ABAX wireless devices (detectors, sirens etc.),

ABAX wireless keypads,

ABAX keyfobs.

-----------------------------------------------

Name - individual name of the device (up to 16 characters).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

No auto-reset after three module tamper alarms - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Response period - communication with wireless devices takes place in specified intervals. The controller is then gathering information on the status of wireless devices and, if necessary, sending commands to the devices, e.g. switching the detectors to their active/passive state, switching on/off the test mode and/or changing configuration of the devices. The response period can be 12, 24 or 36 seconds. The less often communication between the controller and the wireless devices takes place, the more wireless devices can work within each other's operating range (12 seconds - up to 150, 24 seconds - up to 300, 36 seconds - up to 450). Beyond the response period, information about tampers of devices and violations of detectors operating in active mode are sent to the controller. The response period has an effect on the level of energy consumption by the wireless devices. The less often communication between the controller and the wireless devices takes place, the lower energy consumption and the longer battery life are.

Note: In the case of the AMD-103 detector and ASP-100 siren, no communication takes place during polling.

Higher sensitivity for jamming detection - if this option is enabled, the sensitivity of detection of radio communication jamming is boosted.

Zones/Outputs

INT-KWRL

##### Zones/Outputs

Before making any changes, click on the Read button, and after making the changes - on the Write button. The data relating to the wireless devices are stored in the controller and are not read / written when you click on the  /  button in the main menu.

No. - number of the zone/output to which the wireless device is assigned.

Name - name of the zone/output to which the wireless device is assigned.

Type - type/function of the zone/output to which the wireless device is assigned.

Device type - type of the wireless device.

Serial number - serial number of the wireless device.

ARU - parameter available for a wireless device, if the ARU-100 repeater is registered in the controller:

- leave the field blank, if the device is to communicate directly to the controller,

- enter the ARU-100 repeater number in the list of wireless devices, if the device is to communicate to the controller via the repeater (the ARU-100 repeater takes up two positions on the list of devices - enter the number of the first of them).

Always active - the option is available for most of the wireless detectors. It can permanently activate the detector.

Note: The AMD-103 detector and the wireless detectors assigned to 24-h zones are always in the active mode, therefore the Always active option does not have to be enabled for them.

Configuration - see: Configuring the ABAX wireless devices.

Filter - the number of consecutive response periods, during which communication with the device failed to be established, before no communication with the device is reported. Values from the 0 to 50 range can be entered. Entering the digit 0 will disable control of the device presence in the system.

Note: In the case of the AMD-103 magnetic contact and ASP-100 siren, the presence check is performed in a different way than for the other ABAX system devices. If the value programmed for the Filter parameter differs from 0, the lack of presence will be reported if no transmission from the AMD-103 magnetic contact / ASP-100 siren is received within one hour.

Temp. corr. - parameter available for the ATD-100 detector. You can correct the temperature readings by up to ±3.5 °C.

###### Buttons

Read - click to read the data from the controller.

Write - click to write the data to the controller.

Details - click to open the window with the settings of the selected zone (see: Zones).

Identification - click to start the function of identification of devices connected to the expansion modules bus (see: Identification). The button is available after you have added/removed a wireless device.

Test mode - click to start the test mode in the ABAX system. In the test mode:

- LED indicators are enabled in the wireless devices (the LEDs are disabled during normal operation) - information provided by means of the LEDs depends on the device,

- signaling is blocked in the ASP-105 and ASP-205 sirens.

The test mode is started/ended during polling, which results in a delay, its duration depending on the programmed response period. The test mode will be turned off automatically after 30 minutes of:

- starting the test mode from the DLOADX program (the 30-minute period is running from the moment of exiting the controller settings),

- exiting the service mode in the control panel.

Notes:

According to requirements of the EN50131 standard, the level of radio signals sent by wireless devices is reduced during the test mode operation.

For the AMD-103 detector, entering the test mode remotely is not possible.

- click to open Wireless devices window.

- click to open the Exp. modules order window.

Synchronize - click to start the procedure of synchronization, i.e. checking for presence of other ABAX wireless system controllers working within the controller operating range. The controller will synchronize the response period so that the radio transmissions of some controllers should not be mutually jammed. Synchronization is performed automatically upon starting the controller and after each operation of adding/removing devices supported by it.

New device - click to add wireless device (see: Adding wireless device).

Remove device - click to remove wireless device (see: Removing wireless device).

##### INT-KWRL

Before making any changes, click on the Read button, and after making the changes - on the Write button. The data relating to the wireless keypads are stored in the controller and are not read / written when you click on the  /  button in the main menu.

No. - address of the device.

Name - name of the device.

Type - type of the device.

Serial number - serial number of the wireless keypad.

Wake-up - maximum length of time for which the active mode can be started automatically. If you enter a value different from 0:

- the active mode will be started automatically when an alarm occurs or an entry delay, an exit delay or an auto-arming delay begins,

- the CHIME from zones will also be signaled in the inactive mode.

If you enter 0, the active mode will not be started automatically.

Note: If a value different from 0 is preset for the Wake-up parameter, the keypad will be awaiting for transmissions with information on events. As a result, the energy consumption will be growing and the battery life will be considerably reduced.

Card reader - if this option is enabled, the card reader is supported.

Presence contr. - if this option is enabled, the keypad presence is being monitored. If there is no transmission from the keypad for 1 hour, missing keypad will be reported.

###### Buttons

Read - click to read the data from the controller.

Write - click to write the data to the controller.

Keypads identification - click to start the function of identification of devices connected to the keypad bus and wireless keypads enrolled in the ABAX system controllers (Identification). The button is available after you have added a wireless keypad.

Test mode - click to start the test mode in the ABAX system. In the test mode:

- LED indicators are enabled in the wireless devices (the LEDs are disabled during normal operation) - information provided by means of the LEDs depends on the device,

- signaling is blocked in the ASP-105 and ASP-205 sirens.

The test mode is started/ended during polling, which results in a delay, its duration depending on the programmed response period. The test mode will be turned off automatically after 30 minutes of:

- starting the test mode from the DLOADX program (the 30-minute period is running from the moment of exiting the controller settings),

- exiting the service mode in the control panel.

Notes:

According to requirements of the EN50131 standard, the level of radio signals sent by wireless devices is reduced during the test mode operation.

For the AMD-103 detector, entering the test mode remotely is not possible.

- click to open Wireless devices window.

- click to open the Exp. modules order window.

Synchronize - click to start the procedure of synchronization, i.e. checking for presence of other ABAX wireless system controllers working within the controller operating range. The controller will synchronize the response period so that the radio transmissions of some controllers should not be mutually jammed. Synchronization is performed automatically upon starting the controller and after each operation of adding/removing devices supported by it.

New device - click to add wireless keypad (see: Adding wireless keypad).

Remove device - click to remove wireless keypad (see: Removing wireless keypad).

##### Adding wireless device

- Click on the Read button to read the wireless devices data from the controller.

- Click on the New device button. The New wireless dev. window will open.

- Enter the 7-digit serial number of the added device. The serial number can be found on the electronics board or on the enclosure. Each ARF-100 radio signal level tester has serial number 0000500.

- Depending on the device type:

ACX-200 / ACX-201: power-up the expander,

ARF-100: turn on the device,

ASW-100 E / ASW-100 F: insert the controller into 230 V AC socket,

other devices: open the tamper contact.

- The message will confirm that a new device has been added (unless you have entered an invalid serial number, of which you will be informed by a message). It will be assigned to the first free zone from the pool reserved for the controller. The new zone name will be displayed. You can change it. The same name will also be given to the output, if the device is assigned to the output. For some devices, you can also select whether the device will take up one or two positions on the list of devices. Depending on the device, if one position is selected:

- AMD-101 - only additional NC input will be supported,

- AMD-102 - only additional inputs (roller shutter and NC) will be supported;

- AOD-200 - only the motion detector will be supported;

- ATD-100 - you will be able to program only one temperature threshold;

- AVD-100 - only the vibration detector will be supported.

- Click on the OK button (you can click on the Quit button to cancel adding a new device or on the Next button to proceed to adding a next wireless device). The New wireless dev. window will close. The new device will appear in the table.

- Click on the Write button to write the new wireless device data to the controller.

- Click on the Identification button, to start the function of identification of devices connected to the expansion modules bus (the control panel will assign zones / outputs to the wireless devices).

##### Removing wireless device

- Click on the Read button to read the wireless devices data from the controller.

- Click on the device you want to remove (if the device occupies two or more positions on the list, you can click on any of them).

- Click on the Remove device button. The Confirm window will open.

- Click on the Yes button. The Confirm window will close.

- Click on the Write button to save the changes to the controller.

- Click on the Identification button, to start the function of identification of devices connected to the expansion modules bus.

##### Configuring the ABAX wireless devices

Some of the wireless devices provide additional parameters and options, which can be configured by radio (shown in square brackets is information on the zone for which additional parameters can be programmed, if the device takes up more than 1 zone).

AGD-100 (wireless glass-break detector) - enter a digit from the 1 to 3 range to set the sensitivity (1 - low, 2 - medium, 3 - high).

AMD-100 / AMD-101 (wireless magnetic contact) - enter the digit 0 (bottom reed switch) or 1 (side reed switch) to determine which of the two reed switches is to be active.

AMD-102 (wireless magnetic contact with input for roller shutter detector) - for the magnetic contact [first zone], enter the digit 0 (bottom reed switch) or 1 (side reed switch) to determine which of the two reed switches is to be active. For the roller shutter input [second zone], enter 2 digits:

1st digit - number of pulses after which alarm will be triggered by the roller shutter input: from 1 to 8.

2nd digit - time during which the specified number of pulses must occur for the roller shutter input to trigger alarm: 0 (30 seconds), 1 (120 seconds), 2 (240 seconds) or 3 (unlimited duration).

AOCD-250 (wireless outdoor dual technology curtain detector) - enter 2 digits:

1st digit - sensitivity of PIR sensor: from 1 to 4 (1 - minimum; 4 - maximum).

2nd digit - sensitivity of microwave sensor: from 1 to 8 (1 - minimum; 8 - maximum).

AOD-200 (wireless outdoor dual technology motion detector) - for the first position taken by the detector, enter 3 digits:

1st digit - sensitivity of PIR sensor: from 1 to 4 (1 - minimum; 4 - maximum).

2nd digit - sensitivity of microwave sensor: from 1 to 8 (1 - minimum; 8 - maximum).

3rd digit - sensitivity of dusk sensor: from 1 to 4 (1 - minimum; 4 - maximum).

APMD-150 (wireless dual motion detector) - enter 3 digits:

1st digit - sensitivity of PIR sensor: from 1 to 4 (1 - minimum; 4 - maximum).

2nd digit - sensitivity of microwave sensor: from 1 to 8 (1 - minimum; 8 - maximum).

3rd digit - the way of operation in the test mode: 0 (alarm triggered after motion is sensed by both detectors), 1 (alarm triggered after motion is sensed by infrared detector) or 2 (alarm triggered after motion is sensed by microwave detector).

APD-100 (wireless passive infrared detector) - enter 2 digits:

1st digit - sensitivity: 1 (low), 2 (medium) or 3 (high),

2nd digit - pet immunity option: 0 (disabled) or 1 (enabled).

ARD-100 (wireless reorientation detector) - enter a number from the 1 to 16 range to determine sensitivity (1 - minimum; 16 - maximum).

ASD-150 (wireless smoke detector) - enter 2 digits:

1st digit - option to signal alarm from other ASD-150 detectors: 0 (disabled) or 1 (enabled).

2nd digit - option to send out alarm to other ASD-150 detectors: 0 (disabled) or 1 (enabled).

ATD-100 (wireless temperature detector) - for each position taken by the detector, enter in turn:

- letter H (high temperature threshold) or L (low temperature threshold),

- numerical value corresponding to a temperature from the -30° C to +70° C range (with up to 0.5° accuracy),

- numerical value corresponding to a tolerance from the 0.5° C to 10° C range (with up to 0.5° accuracy).

AVD-100 (wireless vibration detector and magnetic contact) - for the magnetic contact [first zone], enter the digit 0 (bottom reed switch) or 1 (side reed switch) to determine which of the two reed switches is to be active. For the vibration detector [second zone], enter 2 digits:

1st digit - sensitivity (registering a single vibration meeting the sensitivity criterion will cause alarm): from 1 to 8 (1 - minimum; 8 - maximum).

2nd digit - number of pulses which, if registered by vibration detector will cause alarm (the pulses need not meet the sensitivity criterion): from 0 to 7. For the value 0, pulses are not counted.

Note: Working parameters of the vibration detector are independently analyzed. The detector can trigger alarm after registering a single, strong vibration caused by a powerful impact, and also on registering several slight vibrations caused by a series of weak strikes.

ASP-100 (wireless outdoor siren) - enter 2 digits:

1st digit - type of acoustic signaling: from 1 to 4.

2nd digit - maximum duration of signaling: 1 (1 minute), 2 (3 minutes), 3 (6 minutes) or 4 (9 minutes).

ASP-105 (wirelessly triggered outdoor siren) - enter 2 digits:

1st digit - type of acoustic signaling: from 1 to 4.

2nd digit - maximum duration of acoustic signaling: 1 (1 minute), 2 (3 minutes), 3 (6 minutes) or 4 (9 minutes).

ASP-205 (wireless indoor siren) - for both positions taken on the list by the siren, enter 3 digits:

1st digit - maximum duration of signaling: 1 (1 minute), 2 (3 minutes), 3 (6 minutes) or 4 (9 minutes).

2nd digit - type of acoustic signaling: 0 (disabled), 1 (sound type 1), 2 (sound type 2) or 3 (sound type 3).

3rd digit - optical signaling: 0 (disabled) or 1 (enabled).

ASW-100 E / ASW-100 F (230 V AC wireless controller) - enter 0 (only remote control of the electric circuit); 1 (remote or manual control of the electric circuit) or 2 (remote or manual control of the electric circuit, but with option to manually block the remote control).

##### Adding wireless keypad

Notes:

Before adding a keypad, make sure that the controller terminals CKM and DTM are connected with the keypad bus of the control panel, and the switch 8 in the controller is set to the OFF position.

The controller allows for enrolling of up to 4 INT-KWRL keypads.

- Click on the Read button to read the data related to wireless keypads from the controller.

- Click on the New device button.

- The New device window will open.

- In the Serial number field enter the serial number of the added keypad. The sticker with serial number you will find on the electronics board.

- In the Address field, select which address is to be assigned to the keypad to be added.

- Press any key on the keypad.

- The message will confirm that a keypad has been added (unless you have entered an invalid serial number, of which you will be informed by a message). The name assigned to the keypad will be displayed. You can change it.

- Click OK (to cancel adding the keypad, click on the Quit button).

- The New device window will close.

- The new keypad will appear in the table in INT-KWRL tab.

- Click on the Keypads identification button (the new keypad must be identified by the control panel).

##### Removing wireless keypad

- Click on the Read button to read the data related to wireless keypads from the controller.

- Click on the wireless keypad you want to remove.

- Click on the Remove device button.

- The Confirm window will open.

- Click on the Yes button.

- The Confirm window will close.

#### INT-VG

INT-VG - voice module.

Voice module allows remote operation of the control panel from the telephone keypad (interactive voice menu). It can store 16 voice messages for telephone messaging.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Content of voice messages - you can enter in the table the content of voice messages that will be used for voice notification. To synthesize these messages, click on the VG-Soft button and start the VG-Soft program (before clicking on the VG-Soft button, save the changes made to the system data file on the computer).

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - the partition in which tamper alarm will be triggered in the event of disconnection of the device from the control panel.

###### Buttons

VG-Soft - the button launches the VG-Soft program, if it is installed on your computer (first time the button is pressed you may need to indicate the access path to the program). The VG-Soft program allows you to manage voice messages and define macro commands in the INT-VG module.

#### CA-64 SM

The following devices are identified as the CA-64 SM:

CA-64 SM - voice synthesizer expander,

INT-VG - voice module, if the DIP-switch 7 is set to ON position.

Voice synthesizer expander can store 16 voice messages for telephone messaging.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Content of voice messages - you can enter in the table the content of voice messages that will be used for voice notification.

No auto-reset after 3 tamp. - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - the partition in which tamper alarm will be triggered in the event of disconnection of the expander from the control panel.

#### INT-KNX

INT-KNX - KNX integration module.

The module enables interfacing of the alarm system with the KNX system.

---------------------------------------------------

Some of the parameters and options are stored in the control panel memory, and some of them in the module memory. Before making any changes, click on the  in the main menu and on the Read button in the window, and after making the changes - on the  in the main menu and on the Write button in the window.

Name - individual name of the device (up to 16 characters).

Physical address - physical address of the BCU port.

Send status every - time interval at which the module is to send information on the status of outputs with the Send option enabled. It can be programmed in minutes or seconds. Entering the value 0 means that the module will not send periodically the output status.

Trouble if KNX bus disconnected - if this option is enabled, when communication with the BCU is lost, the module can report a KNX network communication trouble.

No auto-reset after three module tamper alarms - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

###### Outputs

Parameters for the control of KNX bus devices by virtual outputs are programmed in the module. The other output parameters (output type, cut-off time, etc.) are programmed in the control panel.

No. - the number of output in the system.

Name - the name of output in the system.

Active - how the module will respond to a change in output status:

X - the telegram will be sent to the KNX network,

blank field - no reaction.

Double-click on the field to make changes.

Group address - the output group address (it will be inserted in the telegram sent after activating / deactivating the output).

Telegram type - depending on the selected telegram type:

0. Toggle - on activating the output, a telegram with "On" command is sent, and on deactivating the output, a telegram with "Off" command is sent;

1. Switch ON - on activating the output, a telegram with "On" command is sent;

2. Switch OFF - on deactivating the output, a telegram with "Off" command is sent;

3. Dim increase - on activating the output, a telegram with "Increase, 100%" command is sent, and on deactivating the output - a telegram with "Increase, Break" command;

4. Dim decrease - on activating the output, a telegram with "Decrease, 100%" command is sent, and on deactivating the output - a telegram with "Decrease, Break" command;

5. Set value - on activating the output, a telegram with "Value" command is sent.

Note: When programming the virtual output parameters in the control panel, please note that in case of reverse polarity the above described logic will be reversed.

Value - if the "Set value" type of telegram is selected, you should define the value that will be included in the telegram. You can enter numbers from 0 to 255.

Priority - telegram priority (if two bus elements start transmitting simultaneously, the telegram with higher priority will take precedence).

Send - if the option is enabled, the module will send output status information (see: Send status every parameter).

Read - option for the outputs for which the 0. Toggle telegram type has been selected. If it is enabled, the module will send output status information in reply to a telegram asking about the status.

###### Zones

The parameters related to the control of alarm system zones by KNX bus devices are programmed in the module. The other zone parameters (wiring type, zone type, etc.) are programmed in the control panel. The zone to be controlled by means of telegrams sent by the bus devices should not exist physically. It must have a different wiring type programmed than Not used and Follow output. You can program any zone type (function) for the zone.

Group address - group address, whose presence in the received telegram will enable control of the given zone.

Zone - the number of zone to be controlled by telegrams sent by the bus devices. Receiving a telegram with the "On" command by the INT KNX module will violate the zone (if it has already been violated, its status will not change), and receiving a telegram with the "Off" command will restore the zone (if it has not been violated, its status will not change).

Negation - when this option is active, the logic of zone operation will be reversed (the zone will be violated on receiving a telegram with the "Off" command by the INT KNX module, and the zone restore will occur on receiving a telegram with the "On" command.

Pulse - if this option is enabled, after receiving a telegram wit command:

“On” - the zone will be violated (if it has not been violated) and, after a while, the zone will be restored;

“Off” - the zone restore will occur (if it has been violated) and, after a while, the zone will be violated.

###### Buttons

Read - click to read data from the module.

Write - click to write the data to the module.

Reset - click to restore factory settings to the parameters and options stored in the module memory.

#### INT-KNX-2

INT-KNX-2 - KNX integration module.

The module enables interfacing of the alarm system with the KNX system.

---------------------------------------------------

Some of the parameters and options are stored in the control panel memory, and some of them in the module memory. Before making any changes, click on the  in the main menu and on the Read button in the window, and after making the changes - on the  in the main menu and on the Write button in the window.

Name - individual name of the device (up to 16 characters).

Physical address - address of the INT-KNX-2 module.

KNX comm. delay after reset - the time that must elapse after starting the module, before the module begins sending KNX telegrams.

Two level address - if the option is enabled, the address has a two-level structure. If the option is disabled, the address structure is three-level.

Trouble if KNX bus disconnected - if the option is enabled, the module will report a trouble after loss of communication with the KNX bus.

No auto-reset after three module tamper alarms - if this option is enabled, the feature reducing the number of tamper alarms from the module to three is disabled (the feature prevents multiple logging of the same events and applies to successive uncleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

###### Communication objects

Communication objects are presented in the table. Click on an object to configure its settings in the panel on the right.

No. - number of the alarm system output assigned to the communication object. The output can control the Integra Output communication object. The field is blank if no output is assigned to the communication object (see: DIP-switches).

Type/Name - type of the communication object and name of output / zone / macro command (depending on the selected object type).

Group addresses - group addresses of the communication object.

Flags - each communication object has flags. The default flags should only be changed in exceptional circumstances.

C - Communication

R - Read

W - Write

I - Read on init

T - Transmit

U - Update

Data type - size and meaning of the communication object data.

Priority - priority of the communication object.

Object type - type of the communication object:

none - communication object is not used.

Integra Output - change of output status changes the communication object value.

Integra Zone - change of communication object value changes the zone status.

Virtual (macro) - running the macro command changes the communication object value (without involvement of virtual outputs). The macro command is a sequence of actions, composed of single commands, which are to be done by the control panel when running the macro command. The commands may include instructions to change the value of INT-KNX-2 communication objects. Macro commands are offered by some of the SATEL devices (e.g. INT-KSG, INT-TSG and INT-TSI keypads).

###### Parameters for communication object of Integra Output type

Send on output ON - if the option is enabled, activating the output changes the object value to that entered in the field below.

Send on output OFF - if the option is enabled, deactivating the output changes the object value to that entered in the field below.

Cyclical transmission period - time interval every which updated value of the communication object is sent to the KNX bus. Value 0 means that the object value is not cyclically sent.

###### Parameters for communication object of Integra Zone type

Zone no. - number of the alarm system zone whose status changes with the change of the communication object value.

Reaction on "1" - zone reaction to the object value change to 1:

0. none - zone status will not change,

1: violation - zone will be violated,

2. restore - zone violation will end,

3. impulse - zone will be violated for 5 seconds.

Reaction on "0" - zone reaction to the object value change to 0 (0. none / 1: violation / 2. restore / 3. impulse).

On KNX bus rest. - zone reaction to the KNX bus power restore (0. none / 1: violation / 2. restore).

On KNX bus off - zone reaction to the KNX bus power loss (0. none / 1: violation / 2. restore).

On power up - zone status after starting the module (1: violation / 2. restore).

###### Parameters for communication object of Virtual (macro) type

Name - name of the communication object for the purpose of creating macro commands (up to 16 characters).

Value - value of the communication object after starting the module.

Cyclical transmission period - time interval every which updated value of the communication object is sent to the KNX bus. Value 0 means that the object value is not cyclically sent.

###### Buttons

Read - click to read data from the module.

Write - click to write the data to the module.

Reset - click to restore factory settings to the parameters and options stored in the module memory.

#### INT-AV

INT-AV - audio alarm verification module.

The module enables audio alarm verification to reduce the number of false alarms.

---------------------------------------------------

Name - individual name of the device (up to 16 characters).

Station access phone code - the code the monitoring station operator must enter to be able to initiate the listen-in / talk session.

Verif. after reporting - you can specify for each telephone number of the monitoring station whether, in the event of an alarm, message on the possibility to initiate the listen-in / talk session is to be sent.

Simplified activation - you can specify for each telephone number of the monitoring station whether alarm verification in the line hold mode is to be possible on pressing any key on the phone (receiving any DTMF tone by the control panel). If this option is disabled, alarm verification by the monitoring operator station will only be possible after entering the code. The option is available, if the Verif. after reporting option is enabled for the given telephone number.

Waiting time to call back after the event - the time counted from the moment the monitoring station is informed about the possibility to initiate the listen-in / talk session. Then the control panel is waiting for the monitoring station operator to call back.

Waiting time to call back after 88 command - the time counted from the moment the listen-in / talk session is terminated by the monitoring station operator using the DTMF command, which provides for the possibility of call back. Then the control panel is waiting for the monitoring station operator to call back one more time.

Connection holding time - the time counted after each DTMF tone received by the control panel, during which the phone connection is kept open.

Microphone 1...4 - if this option is enabled, the selected microphone is turned on by default during the listen-in / talk session (sending sounds from the moment the session is started). You can toggle the microphone on / off during the session, using the DTMF command.

Speaker 1...4 - if this option is enabled, the selected speaker is turned on by default during the listen-in / talk session (it can emit sounds from the moment the session is started). You can toggle the speaker on / off during the session, using the DTMF command.

Listen-in only - if this option is enabled, only the listen-in feature is available.

INT-AVT button enabled - if this option is enabled, the button in INT-AVT terminals is supported. Pressing the button on any terminal when the listen-in / talk session lasts will turn on the microphone and the speaker on that terminal and turn them off on all the other terminals.

Connection signaling - if this option is enabled, an interrupted tone will be generated in the handset after establishing connection with the module. This signaling will continue until any DTMF tone is received by the module.

Listen-in only in silent alarm - if this option is enabled, only the listen-in feature will be available in the event of silent alarm.

SATEL standard commands - if this option is enabled, the module can be operated by means of DTMF commands compliant with SATEL standard, and if it is disabled, by means of DTMF commands compliant with SIA standard. All command are described in section DTMF commands.

No auto-reset after three module tamper alarms - it is possible to disable the feature limiting the number of tamper alarms from the module to three (this feature prevents the same events from being repeatedly recorded and applies to consecutive, non-cleared alarms).

Tamper signaled in part. - partition where alarm will be triggered in the event of module tamper.

###### Buttons

Set SIA AV standard - click to set parameters and options of the module, as required by SIA standard.

#### Users of module

###### Administrators

List of administrators. Select the field next to the administrator, if he is to use the module (he will not be able to use the module, unless the field is selected).

###### Users

List of users. Select the field next to the user, if he is to use the module (he will not be able to use the module, unless the field is selected).

#### Exp. modules order

The window enables changing the order of expanders and, consequently, changing the numeration of zones and outputs in those expanders. Such a change may be required, if addressing continuity was not observed when connecting expanders, and a new expander was added, which resulted in a change to numeration of zones or outputs in the system. Thus the existing settings programmed for some zones or outputs became useless.

The numeration changes will only hold good until the expander identification function is re-run.

### Add module

Module - select the type of device you want to add.

Address - select address for the new device.

OK - click to add the selected device and close the window.

Cancel - click to cancel adding the device and close the window.

### Identification

Devices connected to the communication bus and wireless keypads will not be properly supported, unless they have been identified by the control panel.

Identification of the devices is required:

- after the first start-up of the control panel,

- after you have connected a new device to the bus,

- after you have changed an address of the device,

- after you have disconnected a device from the bus,

- after you have enrolled a new wireless device/keypad in the ABAX system controller,

- after you have removed a wireless device from the ABAX system controller.

The identification function should be separately executed for the keypad bus and the expansion module bus.

###### Identification of devices connected to the keypad bus

- Click on the  button in the main menu. The Structure window will open.

- Click on the Hardware tab.

- Click on the Keypads branch.

- Click on the Keypads identification button. This will start the identification function for devices connected to the keypad bus and wireless keypads enrolled in the ABAX system controllers.

- When a window appears to indicate that the identification is completed, click on the OK button.

###### Identification of devices connected to the expansion module bus

- Click on the  button in the main menu. The Structure window will open.

- Click on the Hardware tab.

- Click on the Expansion modules branch.

- Click on the Exp. modules identification button. This will start the identification function for devices connected to both expansion module buses.

- When a window appears to indicate that the identification is completed, click on the OK button.

# Options

Telephone

Printer

Times

Other

Arming

Service

User’s default authority level

## Telephone

Reporting - TELEPHONE - with this option enabled, the control panel can send event codes by means of the telephone line.

Reporting - GPRS - if this option is enabled, the control panel can send event codes via GPRS by using the SATEL GSM module.

Note: The Reporting - GPRS option does not apply to GPRS reporting via the INT-GSM module.

Reporting - ETHM - the option is available if the ETHM-1 Plus / ETHM-1 module is connected to the control panel, but the INT-GSM module is not included in the alarm system. If this option is enabled, the control panel can send event codes over Ethernet by using the ETHM-1 Plus / ETHM-1 module.

Reporting - ETHM/INT-GSM - the option is available if the INT-GSM module is installed in the alarm system. If this option is enabled, the control panel can send event codes via Ethernet by using the ETHM-1 Plus / ETHM-1 module and/or via GPRS and SMS by using the INT-GSM module.

Telephone messaging - if this option is enabled, the control panel can send notifications via the telephone network of the occurrence of specific events using voice or text messages defined by the installer.

SMS messaging - if this option is enabled, the control panel can send event notifications by using SMS messages whose content is created automatically, based on the control panel event log. The SATEL GSM module must be connected to the control panel.

Note: If the INT-GSM module is installed in the alarm system, the SMS messaging option is not available. The SMS messaging option does not apply to SMS messaging by the INT-GSM module.

E-mail messaging - if this option is enabled, the control panel can send event notifications by e-mail messages, the content of which is created automatically, based on descriptions from the control panel event log. The ETHM-1 Plus or INT-GSM module must be connected to the control panel.

Answering - modem - with this option enabled, external initiation of the communication between modem and control panel is possible.

Tone dialing - with this option enabled, the control panel will tone dial the telephone numbers (pulse dial, if this option is disabled).

Ground Start - with this option enabled, the control panel will use the Ground Start method to obtain signal on the telephone line (by grounding temporarily the telephone line wires). Enable this option, if required by your phone service provider.

No dial tone test - with this option enabled, the control panel will not perform the test for dial tone before dialing the number and will start dialing the number 5 seconds after going “off hook”. This makes it possible for the control panel to dial the number when some non-standard tones occur after going off hook (e.g. interrupted tone). When this option is disabled, the control panel will start dialing the number 3 seconds after going off hook, provided that the dial tone is present.

No answer test - with this option enabled, in case of notifying by means of voice messages, the control panel will not perform the test for “off hook” condition. The voice message will be played back 15 seconds after completion of the number dialing.

Double voice message - with this option enabled, the voice message is played back twice during telephone messaging.

Double call - with this option enabled, the control panel must be called twice for the modem communication to be established. The first time you must wait for the preprogrammed number of rings and hang up. Then you must call back within three minutes and the control panel will answer the call immediately. This solution makes it possible to connect after the control panel some additional devices which will be activated after a preset number of rings (e.g. answering machine, fax, etc.).

Pulse dialing 1/1.5 (off 1/2) - this option applies to dialing the telephone numbers by using the pulse mode. Before you enable it, make yourself familiar with the valid standard of pulse dialing.

Answering - audio - with this option enabled, the control panel will carry out the function of call answering.

Note: The Answering - audio option must be enabled, if the users are to operate the alarm system using the interactive voice menu offered by the INT-VG module.

Remote control - with this option enabled, the control panel allows the users having a telephone code to operate the Remote switch outputs by using a phone. The option is available if the Answering - audio is enabled.

External modem - with this option enabled, the control panel will support an external modem connected to the control panel RS-232 port.

Modem ISDN/GSM/ETHM - enable this option if the ETHM-1 Plus / ETHM-1 / INT-GSM / GSM / ISDN module is connected to the control panel RS-232 port. The option is available if the External modem option has been enabled.

Answering - ETHM/GSM - if this option is enabled, it is possible to establish connection with the alarm control panel via the ETHM-1 / ETHM-1 Plus module, INT-GSM module, GSM or ISDN modem. The option is available if the External modem and Modem ISDN/GSM/ETHM options are enabled. The option is not available when the Answering - modem option is enabled, which also enables to establish connection with the alarm control panel via the ETHM-1 / ETHM-1 Plus module, INT-GSM module, GSM or ISDN modem.

Rings before answer - number of rings after which the control panel will go off hook.

## Printer

###### Printout options

Printing - the real-time printing of events on the printer connected to the RS-232 port enabled.

Include reporting status - with this option enabled, on the printout will appear the information if the particular event was sent to the monitoring station (printout of the event information will take place not immediately but after transmission to the station has been completed).

Print names/descriptions - determines if, besides the numbers of zones, outputs, modules and users, also their names and descriptions are to be printed.

Wide paper - printout width will be 132 columns (if the option is disabled: 80 columns).

2400 bps (off:1200 bps) - data will be sent to RS-232 port at a rate of 2400 bps (if the option is disabled - at a rate of 1200 bps).

CR+LF (off: CR) - parameter determining the control mode of paper feed in the printer.

Use parity bit - the parity check of data transferred from the control panel to the printer is enabled.

Parity EVEN (off: ODD) - option determines the mode of parity check of data transferred from the control panel to the printer. The option is relevant only if the Use parity bit option is active.

Notes:

The other parameters of RS-232 transmission are permanently programmed (8 data bits, 1 stop bit).

All the parameters regarding transmission through RS-232 (i.e. transmission rate, CR+LF, parity, data bits and stop bits) are to be set identically on the control panel and on the connected printer. Otherwise the printer will not operate at all, or the printout will be illegible.

###### Printout contents

The options define what kind of information will be contained in the printout.

## Times

Global entry delay - parameter taken into account in the delayed zones, for which the programmed Entry delay is equal to 0.

Global alarm time - time of signaling alarm in keypads, proximity card arm/disarm devices, proximity card readers and DALLAS chip readers.

No armed indication after - time counted from the moment of partition arming, during which information about armed status is displayed on the keypads. Programming the value 0 means that keypads will indicate the armed status as long as the partition is armed.

AC loss report delay - time during which the control panel must not receive AC power so that information of it can be saved to the event log. Having programmed the value 0 means that the information of AC power loss will not be saved to the event log.

Tel. line loss report delay - time during which abnormal voltage must be on the telephone line for the control panel to report the telephone line trouble. A delay in reporting the trouble prevents sending information about short-time voltage dips (e.g. during a phone call) or decays.

Default part. block time - the time period during which the With temporary block type partitions with enabled Default block time option will be blocked.

Summer/winter time - the control panel can automatically adjust the clock settings due to a change from the summer time to the winter time according to the selected schedule.

Summer time from - if the control panel clock is to be corrected by 1 or 2 hours according to dates, you should enter the dates (day, month) after the clock is changed to the summer time (moved forward).

Winter time from - if the control panel clock is to be corrected by 1 or 2 hours according to dates, you should enter the dates (day, month) after the clock is changed to the winter time (moved back).

RTC clock correction - if the accuracy of control panel clock is inadequate, the clock settings may be adjusted once per 24 hours (at midnight) by a defined time. The correction time is programmed in seconds. The maximum correction can be ±19 seconds per 24 hours.

Time server - if the control panel is to synchronize the time with the server (automatically and after suitable function is enabled by the installer or master user), enter the address of time server supporting the NTP protocol. Time synchronization is possible when the ETHM-1 / ETHM-1 Plus / INT-GSM module is connected.

Time zone - if the control panel is to synchronize the time with the server, indicate the time zone, i.e. the difference between the universal time (GMT) and the zone time.

Do not report time server connection trouble - with this option enabled, no trouble will be reported if there is no communication with the time server.

## Other

Permitted “simple” access codes - with this option enabled, with this option enabled, it is possible to use codes containing less than three different digits (e.g. 1111 or 1212) or consisting of consecutive digits (e.g. 3456).

Notify of necessity to change access code - with this option enabled, the keypad will notify the user of the necessity to change access code, if it is known to other users.

Confirm commands with “1” - if this option is enabled, the LCD keypad will require, in case of some functions, additional confirmation with the key 1.

Clear messaging on alarm clearing - with this option enabled, clearing the alarm can automatically cancel messaging about this alarm, if the user clearing the alarm has the Telephone messaging canceling right.

Return to menu from Service Mode - if this option is enabled, exiting the service mode will be followed by return to the user menu instead of to the basic operating mode of the keypad.

Return to menu from menu “Test” - if this option is enabled, exiting the user function available in the Tests or Change options submenu will be followed by return to the submenu instead of to the basic operating mode of the keypad.

Fast module bus communication - it is recommended to enable this option to speed up communication with the modules. The option should only be disabled in case of extended security alarm systems, where electric interference may cause problems with communication.

No module restart reports - when the option is enabled and the Contact ID or SIA format is used for reporting, no event codes referring to module restarts will be sent to the monitoring station.

Service message after tamper alarm - when the option is enabled, after any tamper alarm, the keypads can display on LCD display the message informing that service maintenance is necessary. The message will be cleared after entering the service code and confirming it with the # key.

Backlight off on AC loss - when this option is enabled, the backlighting in keypads can be automatically switched off in case of 230 V AC power loss.

Block keypad after 3 wrong codes - with this option enabled, entering an invalid code (reading in an invalid card / DALLAS iButton) three times will block the keypad (reader) for 90 seconds. After expiry of that time, each next entry of an invalid code (read-in of an invalid card / DALLAS iButton) will block the device immediately.

Trouble memory until review - if the option is enabled, the trouble memory can be signaled until it will be cleared (clearing the trouble memory is possible when exiting the function of viewing troubles in the keypad or in the Troubles window).

Do not show alarm if armed - with this option enabled, no alarms will be indicated in keypads during the armed mode.

Limit events - with this option enabled, while armed events from the same source will be saved into the event log and reported to the monitoring station 3 times only.

Alarming zones review - if this option is enabled, in the LCD keypad the zones that triggered the alarm can be reviewed immediately after the alarm is cleared.

Grade 3 - with this option enabled, the system operates as required by the EN 50131 standard for Grade 3, i.e.:

- starting the arming procedure may be impossible, or, if started, the arming procedure may fail, if some zones are violated in the partition, or there is a trouble in the system,

- LCD keypads, partition keypads, proximity card arm/disarm devices and reader expanders do not signal alarms,

- the  LEDs in keypads indicate alarms only when code has been entered and confirmed with the * key,

- the blinking  LED in keypads means that there is a trouble in the system, some zones are bypassed, or there has been an alarm,

- new access codes in the system must be composed of at least 6 characters (User code min. length parameter),

- information on the arm status is displayed for maximum 60 seconds (No armed indication after parameter),

- the following global options are enabled (cannot be disabled):

Trouble memory until review,

Do not show alarm if armed,

Block keypad after 3 wrong codes,

Warn while arming if trouble,

Display violated/bypassed zones on arming,

Do not report SATEL server connection trouble,

Do not report SMTP server connection trouble,

Do not report time server connection trouble,

- the following global options are disabled (cannot be enabled):

Do not arm if tampered,

Do not arm if battery trouble,

Required System Reset after verified alarm,

Do not arm if trouble,

Do not arm if outputs trouble,

Do not arm if reporting trouble,

- the Tamper alarm always loud option is disabled for all zones, keypad and expander buses (the option cannot be enabled),

- the Valid within 30 sec option is enabled for all partitions (cannot be disabled),

- the entry delay time (global and for individual zones) can be up to 45 seconds (if longer, it will be automatically reduced) for the 0. Entry/Exit, 1. Entry, 2. Delayed, 3. Interior delayed, 85. Entry/Exit - conditional, 86. Entry/Exit - final, 94. Entry/Exit interior and 95. Entry interior zone types,

- the Reporting delay option is enabled for the 4. Perimeter, 5. Instant, 6. Exit, 7. Day/Night and 64...79 Bypassing - group: 1...16 zone types (the option cannot be disabled),

- the Abort delay option is enabled for the 0. Entry/Exit, 1. Entry, 2. Delayed, 3. Interior delayed, 85. Entry/Exit - conditional, 86. Entry/Exit - final, 94. Entry/Exit interior and 95. Entry interior zone types (the option cannot be disabled),

- the Priority option is enabled for the 9. 24h Tamper zone type (the option cannot be disabled),

- the Auto-reset 3 and Auto-reset 1 options are disabled for the 12. Panic audible and 13. Panic silent zone types (the options cannot be enabled),

- AC loss report delay (for the control panel and all modules with power supply units) can be up to 60 minutes (if longer, it will be automatically reduced),

- AC loss report delay (for the control panel and all modules with power supply units) cannot be equal to 0 (if the value 0 is entered, 1 minute will be programmed),

- the quick arming is not possible (relevant parameters in keypads settings are automatically modified),

- the Show arm messages option is enabled in all keypads (it cannot be disabled),

- the following options are disabled in all keypads (they cannot be enabled):

Signaling troubles in partially arm,

Signal new trouble,

Alarm messages: Partitions,

Alarm messages: Zones,

Show violated zones,

Display mode switching,

- it is not possible to view the status of zones, partitions, alarms, trouble memory and current troubles by pressing and holding down the dedicated keypad keys (the corresponding options are disabled and cannot be enabled),

- it is not possible to present information on partition status in the bottom line of keypad display (relevant parameters in the keypad settings will be automatically modified),

- after entering the user menu by means of the service code, you will get access in the Events submenu to the Grade 3 function, which enables viewing the events required by EN 50131 for Grade 3,

- the Isolate user function is only available to the installer,

- the System state user function provides information about alarms, bypassed zones, troubles and partition status (disarmed or type of armed mode).

Tamper if no communication with ABAX device (2h) - with this option enabled, tamper alarm will be triggered if there is no communication with a wireless device of the ABAX system for 2 hours.

No shortcuts in menu - if this option is enabled, the user menu shortcuts are not supported.

Do not report SATEL server connection trouble - if this option is enabled, loss of communication with the SATEL server will not be reported as trouble.

Do not report SMTP server connection trouble - if this option is enabled, the failure sending e-mail will not trigger any trouble signal.

Do not report time server connection trouble - with this option enabled, no trouble will be reported if there is no communication with the time server.

Do not report LAN loss on AC loss - if this option is enabled, trouble will not be reported after Ethernet network loss in the event of control panel AC power failure.

## Arming

Display violated/bypassed zones on arming - if this option is enabled, the user will be informed of the violated / bypassed zones when arming the system from keypad.

Notes:

If the system is being armed in the “full + bypasses” mode, bypasses and violations of the zones for which the Bypassed if no exit option is enabled are not checked.

If the system is being armed in the “without interior” or “without interior and without entry delay” mode, bypasses and violations of the 3. Interior delayed type zones are not checked (unless the Delay in 2&3 type arming option is enabled for the zone).

Warn while arming if trouble - if this option is enabled, the user will be informed of the existing troubles, if any, when arming the system from keypad.

Do not arm if tampered - if this option is enabled, arming will be impossible if a tamper is discovered.

Do not arm if reporting trouble - if this option is enabled, arming will be impossible in case of any problems with reporting.

Do not arm if battery trouble - if this option is enabled, arming will be impossible in case of a battery failure.

Do not arm if outputs trouble - if this option is enabled, arming will be impossible when the control panel detects that the mainboard outputs are overloaded or devices connected to these outputs are cut off.

Do not arm if trouble - if this option is enabled, arming will be impossible in case of a trouble.

Required system reset after verified alarm - if this option is enabled, arming will be impossible after a verified alarm.

Note: The options Do not arm if tampered, Do not arm if battery trouble, Do not arm if trouble, Do not arm if outputs trouble and Do not arm if reporting trouble are available, when the Warn while arming if trouble option is enabled.

## Service

Service access code - a code that allows access to the service mode, as well as some functions in the user menu.

Disable service mode - with this option enabled, entering the service mode “from pins” (by hardware means) will be impossible (entering the service mode “from pins” will only be possible if the control panel factory settings are restored).

Disable downloading - with this option enabled, starting communication with the DLOADX program “from pins” will be impossible.

Hide service mode after - the time counted from the last operation performed in the service menu, after expiry of which the service mode menu will be hidden. If value 0 is programmed, the automatic hiding of the service mode will be disabled.

Service mode beep - with this option enabled, the service mode will be acoustically signaled in the keypad.

User code min. length - the minimum required number of digits in the user code. The parameter will be taken into account when creating and editing the codes (but it has no effect on the codes already existing in the system).

## User’s default authority level

You can define which user rights will be automatically assigned to a new user. The list of permissions can be modified during user creating or editing.

# Zones

Zone - 1. a separated part of the protected area that can supervised by a detector or detectors. 2. the terminals on control panel/expander electronics board to which you can connect a detector or another device whose state is to be supervised (panic button, siren tamper contact, power supply output indicating loss of 230 V AC supply, etc.).

A zone can only be assigned to one partition.

The system supports the following zones:

hardwired - on the control panel electronics board, in keypads and expanders. The number of available hardwired zones is determined by the control panel during identification procedure.

wireless - when the ACU-120, ACU-270, ACU-100 or ACU-250 controller is connected. The number of available wireless zones depends on the number of wireless devices registered in the system and is determined during the procedure of adding the devices.

virtual - zones which physically do not exist, but have been programmed as Follow output or are controlled by means of a keyfob.

---------------------------------------------------

Zone name - individual name of the zone (up to 16 characters).

Assigned to - partition to which the zone belongs.

Zone type - see: Zone types.

Entry delay - refers to the delayed zones (including the zone types: 0. Entry/Exit, 1. Entry, 2. Delayed, 3. Interior delayed, 85. Entry/Exit - conditional, 86. Entry/Exit - final, 94. Entry/Exit interior and 95. Entry interior). The alarm from the zone will be delayed by a preset time. This makes it possible to disarm the partition before the alarm is triggered.

Signaling delay - refers to the 4. Perimeter, 5. Instant and 6. Exit type zones. Loud alarm signaling can be delayed by a programmed time period.

Alarm delay - refers to the 5. Instant and 6. Exit type zones. The alarm from zone may be delayed by a programmed time period.

Surveillance time - refers to the 8. Exterior type zones.

Bypass time - refers to the bypassing zones (zone types 64-79). It indicates for how long the zones will be bypassed. If value 0 is programmed, the zones will remain bypassed until disarming the partitions to which they belong, or until they are unbypassed by the user.

Module number (lock/keypad) - refers to the 58. Technical - Door button type zones. It defines which door will be unlocked after zone violation (you can indicate a door controlled by partition keypad, code lock, proximity card reader expander or DALLAS chip reader expander).

Arming mode - refers to the 80. Arming and 82. Arm/Disarm type zones. It defines which type of armed mode will be activated by the zone:

0 - full armed mode,

1 - fully armed and, additionally, the zones for which the Bypassed if no exit option is enabled, will be bypassed,

2 - 3. Interior delayed type zones will not be armed, 8. Exterior will trigger silent alarm, and the other ones - audible alarm,

3 - same as 2, but the delayed zones type will act as instant ones.

Group - refers to the 80. Arming, 81. Disarming and 83. Clearing alarm type zones. It defines which group of partitions will be controlled by the zone (the zone always controls the partition it belongs to). If value 0 is programmed, the zone will only control the partition to which it belongs.

Exit delay - refers to the 89. Finishing exit delay type zones.

Outputs group - refers to the 92. Outputs group off type zones.

Wiring type - must be selected to match the detector type and how it is connected to the zone:

0. no detector - no detector is connected to the zone,

1. NC - the zone supports a detector of NC (normally closed) type,

2. NO - the zone supports a detector of NO (normally open) type,

3. EOL - the zone supports a detector of NO or NC type with EOL resistor in the circuit,

4. 2EOL/NC - the zone supports a detector of NC type with two EOL resistors in the circuit,

5. 2EOL/NO - the zone supports a detector of NO type with two EOL resistors in the circuit,

6. Roller - the zone supports a roller shutter detector,

7. Vibration - the zone supports a vibration detector (also NC type detector),

8. Follow output - the zone does not support any detectors - its status depends solely on the status of selected output (physical violations and tampers of the zone are ignored),

9. Roller 2EOL - the zone supports a roller shutter detector with two EOL resistors in the circuit,

10. Vibration 2EOL - the zone supports a vibration detector (also NC type detector) with two EOL resistors in the circuit,

11. 3EOL/NC - the zone supports a detector of NC type with three EOL resistors in the circuit,

12. 3EOL/NO - the zone supports a detector of NO type with three EOL resistors in the circuit.

Zone sensitivity - depending on wiring type:

NO, NC, EOL, 2EOL/NC, 2EOL/NO, 3EOL/NC and 3EOL/NO - the time during which the zone must be violated, so that it can be noted by the control panel.

Roller / Roller 2EOL - 2 parameters are to be programmed (in the DLOADX program, you should enter two numbers in the Zone sensitivity field):

Pulses duration - the time period during which a specified number of pulses must occur (Pulses count) for the zone to be violated. You can enter 0 (the pulse counter will only be reset on arming / disarming), 1 (30 seconds), 2 (120 seconds) or 3 (240 seconds).

Pulses count - the number of pulses after which the zone will be violated. You can program values from 1 to 8.

Vibration / Vibration 2EOL - 2 parameters are to be programmed (in the DLOADX program, you should enter two numbers in the Zone sensitivity field):

Sensitivity - occurrence of a pulse whose duration is equal to or longer than the defined time will cause violation of the zone. You can program values from the 3 ms to 96 ms range (every 3 ms).

Pulses count - the number of pulses after which the zone will be violated. You can program values from 0 to 7. If the value 0 is programmed, the pulses will not be counted - only Sensitivity will be taken into account.

Output - refers to the Follow output wiring type. Indicate the number of output whose activation will violate the zone. The output can be a virtual one.

Max. violation time / Max. door opening time - exceeding the maximum time of violation/door opening is recognized by the control panel as a detector failure/door failure. If the value 0 is programmed, control of this time is disabled.

Max. no violation time - exceeding the maximum time of no violation is recognized by the control panel as a detector failure. The time will only be counted when the zone is disarmed. If the value 0 is programmed, control of this time is disabled. The time can be programmed in hours or minutes.

Note: It is recommended that you program the Max. no violation time parameter, since it will provide an additional supervision of the detector connected to the zone.

###### Options

Power up delay - when the option is enabled, the zone will be bypassed for 120 sec. after power-up (which prevents triggering alarms e.g. when starting the alarm control panel).

Priority - when this option is enabled, arming will be impossible, if the zone is violated (e.g. windows have been left open, etc.).

Contr. by pulse(off-by state) - option for 82. Arm/Disarm zone type. If it is enabled, violation of the zone will arm/disarm the partition (depending on the current status of the partition). If the option is disabled, zone violation will arm, and the zone restore will disarm the partition.

Video on disarmed - if this option is enabled, violating the zone when the partition is disarmed will activate the 15. Video on disarmed type output.

Video on armed - if this option is enabled, violating the zone when the partition is armed will activate the 16. Video on armed type output.

Bypass disabled - if this option is enabled, the user cannot bypass the zone.

Bypassed if no exit - if this option is enabled, the zone will be automatically bypassed, when no partition exit is registered during the partition exit delay countdown. The zone will also be bypassed when the “full + bypasses” arming mode is on (registering a partition exit is irrelevant then). The zone will be unbypassed after the partition is disarmed.

Auto-reset 3 - with this option enabled, the zone can trigger up to 3 alarms. As long as the alarm is not cleared or the partition is not armed/disarmed, violations of the zone will not trigger any alarm.

Auto-reset 1 - with this option enabled, the zone can trigger only 1 alarm. As long as the alarm is not cleared or the partition is not armed/disarmed, violations of the zone will not trigger any alarm.

Clearing Autoreset - with this option enabled, alarm counters for the zones for which the Auto-reset 3 or Auto-reset 1 option is enabled can be automatically reset at midnight (violations of these zones will be able to trigger alarms again).

Pre-alarm - if this option is enabled, alarms from the zone will be verified.

With verification - an option for the zone types 0-2, 85-86 and 94-95. If it is enabled, alarms from the zone will be verified.

Note: Alarm from the zone with enabled Pre-alarm or With verification option will be an unverified alarm, unless during verification (see description of the Alarm verification time parameter) an alarm will be caused by another zone with enabled Pre-alarm or With verification option. In such a case, a verified alarm will be triggered.

No restore event - option for the 47. No alarm action zone type with Store to event log and No reporting options enabled. If it is enabled, the zone restore is not stored into the event log.

Delay in 2&3 type arming - an option for the 3. Interior delayed zone type. If the option is enabled, the zone will be armed and act as a delayed one upon activation of the type 2 (without interior) and type 3 (without interior and without entry delay) arm mode.

Bell delay - an option for the zone types 5 and 6. It changes the way of reaction to a zone violation when armed. If the option is disabled, the alarm from zone will be delayed by a programmed time period (Alarm delay). If the option is enabled, the zone will alarm immediately (event, reporting and telephone messaging), but the loud signaling will be delayed by a programmed time period (Signaling delay).

Alarm in arm state - an option for the zone types 64-79. It is available, if the No bypass if armed option is enabled. When it is enabled, violating an armed zone will cause an alarm (if the partition exit was registered upon arming).

Alarm clearing - an option for the zone types 81 and 82. With this option enabled, violation of the zone will clear alarm in the partition, if it is currently indicated.

Restore disarms - option for the 89. Finishing exit delay zone type. If it is enabled, the zone restore will disarm the partition. This option overrides the option Restore disables verif.

Alarming - option available for the 91. Detector mask zone type. If enabled, violation of the zone will additionally trigger an alarm.

Blocks verification - option for 0-2, 85-86 and 94-95 zone types. If it is enabled, violation of the zone will block verification of alarms in the partition. All alarms will be unverified until the partition is armed again.

Reporting delay - option for the 4-7 and 64-79 zone types. Violation of the zone during the entry delay countdown will trigger a warning alarm. The warning alarm does not cause any loud alarm signal and is not reported. It can be signaled by the outputs of 9. DAY Alarm, 12. Silent alarm and 116. Internal siren type. If the zone is not disarmed within 30 seconds, the entry delay has expired or another instant is violated, the burglary alarm will be triggered.

Check arm possibility - option for the arming zones (80 and 82 zone types). The zone will not arm, if a zone with enabled Priority option is violated in the partition, or other circumstance have occurred which prevent arming (depending on the selected options, tamper, trouble, etc.).

Restore disables verif. - option for the 89. Finishing exit delay zone type. If it is enabled, the zone restore will disable verification of alarms in the partition. All alarms will be unverified until the partition is armed again.

Abort delay - when this option is enabled, violating the zone during the entry delay countdown will result in registering a “Zone violation” event (this event can only be reported in the 4/2 format). When the option is disabled, violating the zone during the entry delay countdown will result in registering an “Alarm” event (this event is reported and initiates messaging).

Report if not armed - option for the 7. Day/Night zone type. If it is enabled, the alarm will be reported at all times. If it is disabled, the alarm will only be reported if the zone is armed. If the zone is disarmed, the zone violation will trigger a warning alarm. The warning alarm does not cause any loud alarm signal and is not reported. It can be signaled by the 9. DAY Alarm, 12. Silent alarm and 116. Internal siren type outputs.

No reporting - option for the 47. No alarm action zone type with the Store to event log option enabled:

- enabled - violation of the zone will write an event informing about zone violation,

- disabled - violation of the zone will result in writing an event informing about keybox opening, the code of which is sent to the monitoring station.

Event: arming failed - option for 80. Arming and 82. Arm/Disarm zone types. If this option is enabled, unsuccessful arming by means of zone is saved to the event log.

Partition temporary blocking - option for the 84. Guard zone type. If it is enabled, violation of the zone will block the partition for the time of guard round.

Disabled in arm state - option for the 91. Detector mask zone type. If the option is enabled and the zone is violated when armed, the information on detector trouble (masking) will not be stored into the event log (the event code will not be sent to the monitoring station).

Restore after bell - with this option enabled, the zone restore code will be reported to the central monitoring station only after the alarm signaling is ended.

Restore after disarm - with this option enabled, the zone restore code will be reported to the central monitoring station only after disarming the partition to which the zone belongs.

Alarm on exit delay end - with this option enabled, the zone will trigger alarm if it is violated at the moment of ending the exit delay countdown. If the option is disabled, the alarm will only be triggered in case of changing the zone status from normal to violated when armed.

Store to event log - option for the 47. No alarm action and 63. Trouble zone types. If it is enabled, violation of the zone will result in storing an event according to the zone type (in case of the 47. No alarm action zone type, the information to be written depends additionally on the No reporting option).

No bypass if armed - option for the 64-79 zone types. If it is enabled, violation of the armed zone will block no group of zones (provided that during the exit delay countdown an exit from the partition is recorded).

Messaging cancelling - option for the 81-83 zone types. If it is enabled, violation of the zone will cancel the messaging, if it is currently ongoing.

Alarm on unbypass - if the option is enabled and the armed zone is violated after being bypassed, an alarm will be triggered.

Store event only if armed - option for the 47. No alarm action zone type. It is available, if the Store to event log option is enabled. If it is enabled, violations of the zone will be written into the event log, provided that the partition to which the zone is assigned, is armed.

Tamper alarm always loud - if this option is enabled, tamper alarm is always loud (if option is disabled - tamper alarm is loud only when armed).

CHIME in module - with this option enabled, zone violation can be signaled in partition keypads, code locks and readers expanders assigned to the same partition as the zone (the option Chime must be enabled in the expander).

No alarm sign. in keypad - option for 13. Panic-silent zone type. If it is enabled, alarm from this zone will not be signaled on keypads. Clearing this alarm by means of keypad will not be possible.

Note: Outputs signaling the silent panic alarm can be deactivated using the Clear latched outputs user function.

Counters

Bypasses

Arm/Disarm groups

## Zone types

0. Entry/Exit - a delayed zone combining two functions:

entry - violation of the zone starts entry delay counting in the partition and turns on delay for the 3. Interior delayed type zones,

exit - violation of the zone during exit delay countdown is equivalent to the partition exit.

1. Entry - violation of the zone starts entry delay counting in the partition and turns on delay for the 3. Interior delayed type zones.

2. Delayed - a delayed-action zone with optional signaling of delay countdown in keypads.

3. Interior delayed - the zone operates as a delayed one when:

- violation of another zone has triggered the entry delay countdown in the partition,

- the delay will be activated using the INT-ENT entry keypad,

- arm mode type 2 or 3 is active and the Delay in 2&3 type arming option is enabled for the zone.

In other situations, the zone will act as an instant one.

4. Perimeter - instant zone, which is already armed during exit delay countdown.

5. Instant - instant zone.

6. Exit - violation of the zone during exit delay countdown is equivalent to the partition exit.

7. Day/Night - if disarmed, the zone will signal violation acoustically in keypads and on the 9. DAY Alarm, 12. Silent alarm and 116. Internal Siren outputs. When armed, the zone acts as the 5. Instant zone.

8. Exterior - a zone with alarm verification: zone violation will start counting the surveillance time - if a second violation takes place during this time, an alarm will be triggered. If the Surveillance time is not programmed (the value 0 is entered), the alarm will be generated upon the first violation.

9. 24h Tamper - permanently armed zone, intended for the tamper circuits. The zone violation will additionally cause a trouble condition.

10. 24h Vibration - permanently armed zone, intended for working with vibration detectors.

Note: If the partition includes the 10. 24h Vibration zone, starting the procedure of arming from the LCD keypad will initiate a test of vibration detectors (the 39. Test vibration detectors output is activated and the countdown of time remained to the test end is running).

11. 24h Cash machine - permanently armed zone, intended for protection of a cash machine.

12. PANIC-audible - permanently armed zone, intended for operating the panic buttons.

13. PANIC-silent - permanently armed zone, intended for operating the panic buttons. Violating the zone will trigger a silent alarm.

14. Medical - Button

15. Personal emergency

The zone types 14 and 15 trigger alarm signaled in the LCD keypads and on the 12. Silent alarm outputs. The names of zones and codes of events from these zones are consistent with the Contact ID reporting format.

16...31 Counting C1...16 - the counting zones will signal an alarm when the number of violations counted during a specified time period exceeds the set value (see: Counters). Violations of the counting zones in armed mode can be signaled at the 9. DAY Alarm, 12. Silent alarm and 116. Internal Siren outputs.

32. 24h Fire

33. 24h Fire - Smoke

34. 24h Fire - Combustion

35. 24h Fire - Water flow (fire)

36. 24h Fire - Heat

37. 24h Fire - Pull station

38. 24h Fire - Duct

39. 24h Fire - Flame

The zone types from 32 to 39 cause a fire alarm. The names of zones and codes of events from these zones are consistent with the Contact ID reporting format. The fire zones (except for 24h Fire - Button) can work with alarm verification.

40. 24h Fire supervisory

41. 24h Low water pressure

42. 24h Low CO2

43. 24h Water valve detector

44. 24h Low water level

45. 24h Pump activated

46. 24h Pump failure

47. No alarm action - may be used to control the outputs. Additional options (Store to event log, No reporting and Store event only if armed) enable the zone to be used for other applications e.g. supervising the keybox.

48. 24h auxiliary - Protection loop

49. 24h auxiliary - Gas detector

50. 24h auxiliary - Refrigeration

51. 24h auxiliary - Loss of heat

52. 24h auxiliary - Water leakage

53. 24h auxiliary - Foil break

54. 24h auxiliary - Low bottled gas level

55. 24h auxiliary - High temperature

56. 24h auxiliary - Low temperature

57. Technical - Door open - zone intended for supervising the status of the door defined as Dependent door in the module executing the access control functions (partition keypad, code lock, readers expander).

58. Technical - Door button - zone violation will result in opening the door controlled by the module executing the access control functions (partition keypad, code lock, readers expander).

59. Technical - AC loss - intended for control of devices working together with the alarm control panel e.g. additional power supply units. Violation of the zone will cause a trouble condition.

60. Technical - BATTERY low - intended for control of the batteries of additional power supply units working in conjunction with the control panel. Violation of the zone will cause a trouble condition.

61. Technical - GSM link trouble - intended for control of the external GSM communication module. Violation of the zone will cause a trouble condition.

62. Technical - overload - intended for control of an additional power supply unit used together with the control unit. Violation of the zone will cause a trouble condition.

63. Trouble - violation of the zone will cause a trouble condition.

64...79 Bypassing - group: 1-16 - violation of this type of zone can bypass a group of zones (see: Bypasses).

80. Arming - violation of the zone will arm the partition to which the zone belongs. Additionally, you can select a group of partitions which will also be armed (see: Arm/Disarm groups).

81. Disarming - violation of the zone will disarm the partition to which the zone belongs. Additionally, you can select a group of partitions which will also be disarmed (see: Arm/Disarm groups).

82. Arm/Disarm - the zone controls the arming status of the partition it belongs to. The control mode depends on the Contr. by pulse(off-by state) option. Disarming may simultaneously clear the alarm and cancel the messaging.

83. Clearing alarm - violation of the zone will clear alarm in the selected group of partitions (see: Arm/Disarm groups) or the partition to which the zone belongs, and can also cancel messaging.

84. Guard - violation of the zone is recognized as recording the guard's round in the partition to which the zone belongs.

85. Entry/Exit - conditional - similarly as the 0. Entry/Exit type with an extra feature: the zone becomes an instant one upon arming, if no partition exit is registered upon starting the arming procedure.

86. Entry/Exit - final - similarly as the 0. Entry/Exit, but the zone restore during exit delay countdown will terminate the exit delay countdown and arm the system.

87. Exit - final - similarly as the 6. Exit, but the zone restore during exit delay countdown will terminate the exit delay countdown and arm the system.

88. 24h burglary - a permanently armed zone. Its violation will cause the burglary alarm.

89. Finishing exit delay - zone violation will reduce the partition exit delay time. It is possible to program a shorter exit delay time. If this value remains not programmed, the exit time will be reduced to 4 seconds from the zone violation. There will be no effect if the zone is violated and the just running exit delay is shorter than that programmed for the zone.

90. Disabling verification - zone violation will disable verification of alarms in the partition. All alarms will be unverified until next arming.

91. Detector mask - the permanently armed zone, dedicated to anti-masking control. Violation of the zone will be treated by the control panel as detector trouble (masking).

92. Outputs group off - the zone allows to deactivate a selected group of outputs.

93. Outputs group ON - the zone allows to activate a selected group of outputs.

94. Entry/Exit interior - similarly as the 0. Entry/Exit, but it will only be armed in the case of full armed status (arming modes 0 and 1).

95. Entry interior - similarly as the 1. Entry, but it will only be armed in the case of full armed status (arming modes 0 and 1).

96. Fire monitoring - permanently armed zone. After the zone is violated, fire alarm information is saved to the control panel memory.

97. Fire panel fault. monit. - permanently armed zone. After the zone is violated, an event is saved to the control panel memory.

## Counters

The control panel makes it possible to program 16 different counters which determine the operating mode of the counter zones (zone types 16-31).

Max. value - number of violations which, if exceeded, will trigger an alarm.

Counting time - the time in which violations are counted.

Counter type:

normal - all violations of counter group zones are counted,

omit recurs - skips violations of the same zone (the alarm will be triggered, if the number of violations of different zones exceeds the maximum value).

Note: If the counter skips repeats, the programmed Maximum counter value must be lower than the number of zones in counter group.

Assigned zones - numbers of zones that are assigned to the counter.

## Bypasses

You can define a group of zones for each of the zone types from 64 to 79.

The numbers of fields in the table correspond to those of zones. The field color has the following meanings:

white - the zone does not belong to the group,

orange - the zone belongs to the group.

Double-click on the field to change its color.

Having assigned the zones to a group, define what reaction should be to violation of the bypassing zone:

Bypass only - the zones belonging to the group will be bypassed for Bypass time (see: Zones).

Bypass on/off - the zones belonging to the group will remain bypassed as long as the bypassing zone is violated (they can be bypassed by the user).

## Arm/Disarm groups

You can define up to 16 partition groups which will be controlled using the 80. Arming, 81. Disarming and 83. Clearing alarm type zones.

The numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the partition does not belong to the group,

orange - the partition belongs to the group.

Double-click on the field to change its color.

# Outputs

Using the outputs, the control panel controls the operation of external devices.

The system supports the following outputs:

hardwired - on the control panel electronics board and in expanders. The number of available hardwired outputs is determined by the control panel during identification procedure.

wireless - after connecting the ACU-120, ACU-270, ACU-100 or ACU-250 controller. The number of available wireless outputs depends on the number of wireless devices registered in the system and is determined during the procedure of adding wireless devices.

virtual - the outputs which do not exist physically, but can be used e.g. for execution of logical functions.

---------------------------------------------------

Output name - individual name of the output (up to 16 characters).

Output function - see: Output functions.

Cut off time - time during which the output is active. The cut-off time can be programmed with an accuracy of up to 0.1 second. The parameter is irrelevant for the status indicating outputs.

Note: If you want to set the cut-off time with an accuracy of up to 0.1 sec, right-click on the “Cut off time” column. A pop-up menu will appear, in which you must click on “Edit”.

State indication - instead of the output state, the state of selected zone can be displayed. This can be useful if the output is activated just for a short while to turn on / off a device and the device state is supervised by the control panel zone.

Note: The output status cannot be presented according to the zone 256 status.

Pol.+ - defines the output operating mode (see Table below).

|  | high-current output |
| --- | --- |
|  | option enabled (normal polarity) | option disabled (reversed polarity) |
| active status | +12V voltage supply | +12V voltage cut-off |
| inactive status | +12V voltage cut-off | +12V voltage supply |
|  | low-current output |
|  | option enabled (normal polarity) | option disabled (reversed polarity) |
| active status | shorted to ground | isolated from ground |
| inactive status | isolated from ground | shorted to ground |

Pulsating - the option refers to timed outputs. If it is enabled, the output operates in a pulsating mode. If it is disabled, the output operates continuously.

Latch - the option refers to alarm outputs. If it is enabled, the output will be active until the alarm is cleared by the user.

Timers set - if this option is enabled, timers from 33 to 64 can control the output (if the option is disabled - from 1 to 32).

Active during violation - the option applies to the 24. MONO switch output. If enabled, the output is always active when a control zone is violated, and the countdown of output cut-off time will only be running after the violation ends.

Timer activates/deactivates - the option applies to the 24. MONO switch and 25. BI switch outputs. If enabled, the output can be controlled by selected timers. Turning the timer ON activates the output (in case of the 24. MONO switch type output - for a programmed time), and turning the timer OFF deactivates the output.

Not controlled by arming - the option refers to the 105. Shutter up and 106. Shutter down type outputs. If enabled, the partition arming / disarming has no effect on the output status.

Temperature T1 - the parameters refers to the 120. Thermostat type output. The first temperature threshold. It is active when all control timers are OFF or the forcing output is active. If the temperature threshold is active, the output will be turned on if the temperature drops below the threshold.

Temperature T2 - the parameters refers to the 120. Thermostat type output. The second temperature threshold. It is active when the control timer is ON or the forcing output is inactive. If the temperature threshold is active, the output will be turned on if the temperature drops below the threshold.

Hysteresis - the parameters refers to the 120. Thermostat type output. Temperature difference between the preset temperature threshold and the temperature of actual turning the output on or off. Hysteresis is intended to eliminate the undesirable changes of output status in case of temperature variations. The output will be turned on when the temperature drops below the threshold by the hysteresis value. The output will be turned off when the temperature rises above the threshold by the hysteresis value. Programming “0” means that hysteresis is equal to 0.5(C.

Output forcing T1 - the parameters refers to the 120. Thermostat type output. You can indicate the output which will force the first temperature threshold. If the output is active, the first temperature threshold will be active. When the output is inactive, the control timers will decide which temperature threshold is active.

Note: The output 256 cannot be indicated as the forcing one.

###### Output triggering

Methods of triggering the highlighted output are presented in tabular form. The field color has the following meanings:

white - the field not selected,

orange - the field selected.

Double-click on the field to change its color.

The field numbers correspond to:

Zones - numbers of the zones.

LCD keypads - addresses of the keypads.

From Part./Part. Keypads - numbers of the partitions.

TIMERS - numbers of the timers.

Expansion modules - addresses of the expansion modules.

Mimic boards - addresses of the mimic boards.

Indicates - types of the troubles - a single click will display information on what trouble is assigned to the field.

Telephone usage type - the methods of using the telephone communicator - a single click will display information on what method of using the telephone communicator is assigned to the field.

Reset zones - numbers of the zones.

OUTPUTS - numbers of the outputs.

Administrators - numbers of the administrators.

Users - numbers of the users.

PING test error - addresses of the Ethernet modules.

No Ethernet connection - addresses of the Ethernet modules.

Voice message - numbers of the voice messages.

Remote switch - numbers of the remote switches.

Wireless devices - numbers of the zones (highlight the zones to which wireless devices are assigned).

Burg. zones in part. / Fire/techn. zones in part. - numbers of the partitions.

Arm mode - arming modes - a single click will display information on what arming mode is assigned to the field.

Exp.Module-bus 1 / Exp.Module-bus 2 - addresses of the expansion modules.

Temperature detector - numbers of the zones (highlight the zones to which ATD-100 temperature detectors are assigned).

Timers controlling T1/T2 - numbers of the timers (the parameter applies to 120. Thermostat type outputs - when the control timer is ON, the second temperature threshold will be active, unless the forcing output is active).

###### Blocked in partitions

Table displayed in case of the 11. Chime type outputs. The numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the output cannot be blocked in partition,

orange - the output can be blocked in partition (users having access to the partition can block the output using the Outputs chime function).

Double-click on the field to change its color.

###### Clearing

Table displayed in case of the alarm outputs. The numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - the alarm cannot be cleared in partition,

orange - the alarm can be cleared in partition (the users having access to the partition will be able to clear the alarm).

Double-click on the field to change its color.

Note: The alarm must be signaled in the partition where it is to be cleared. If no alarm is being signaled by the given partition, it will be impossible to clear it.

###### Disabling timers

Table displayed in the case of 105. Shutter up and 106. Shutter down type outputs. The numbers of fields in the table correspond to those of timers. The field color has the following meanings:

white - the timer does not affect output operation,

orange - when the timer is active, disarming (105. Shutter up) / arming (106. Shutter down) will not activate the output.

Double-click on the field to change its color.

###### Buttons

Previous - click to go to previous output settings.

Next - click to go to next output settings.

Output groups - click to open the Output groups window.

## Output functions

0. Not used

1. Burglary - signals all burglary and panic alarms (from zones, keypad/expander tamper, keypad Panic, etc.).

2. Fire/burglary - signals the burglary and panic alarms (continuous sound) and the fire alarms (intermittent sound).

3. Fire alarm - signals the fire alarms (from fire zones and triggered from keypads).

4. Keypad alarm - signals the alarms triggered from keypad: fire, medical (auxiliary) and panic (except: silent panic alarm).

5. Fire (from keypad) - signals the fire alarms triggered from keypad.

6. Panic (from keypad) - signals the loud panic alarms triggered from keypad.

7. Medical alarm (from keypad) - signals the medical assistance call alarm triggered from keypad.

8. Tamper alarm - signals the tamper alarms.

9. DAY alarm - signals the following:

- alarms from 13. PANIC-silent type zones,

- medical alarms from the 14. Medical - Button and 15. Personal emergency type zones,

- alarms from 7. Day/Night type zones, if the partition to which the zone belongs is disarmed,

- alarms from 8. Exterior type zones, if the armed mode which assumes that the user will stay inside the protected facility is enabled in the partition,

- alarms from 4. Perimeter type zones, if the Signaling delay has been programmed for them,

- alarm from 5. Instant and 6. Exit type zones, if the Bell delay option has been enabled and the Signaling delay has been programmed for them,

- alarms from zones, for which the Reporting delay option has been enabled, provided they were violated during the Entry delay countdown,

- unverified alarms, if the Audible alarm after verification option is enabled for the partition,

- the first violation of the 8. Exterior type zones when they are armed, provided the Surveillance time has been programmed for the zone,

- violation of the counting zones (16-31 type zones) when armed.

10. DURESS alarm - action carried out under duress - signals that a DURESS type code (or prefix) has been used in the system.

11. Chime - signals violation of the zones when they are disarmed.

12. Silent alarm - activates in the same situations as the 9. DAY Alarm output. Additionally, it can signal silent panic alarms.

13. Technical alarm - signals alarms from zone types 40-56.

14. Zone violation - indicates the violations of zones.

15. Video on disarmed - controlled by zones with the Video on disarmed option enabled.

16. Video on armed - controlled by zones with the Video on armed option enabled.

17. READY status - indicates whether the system is ready for arming, i.e. whether there are no violated zones (active when there is no violation).

18. BYPASS status - indicates the bypassing of zones.

19. Exit delay status - indicates the Exit delay countdown.

20. Entry delay status - indicates the Entry delay countdown.

21. Armed status - indicates the armed status of partitions.

22. Full armed status - active if all selected partitions are armed.

23. Arm/Disarm beep - signals:

- starting the arming procedure (arming, if the exit delay has not been programmed) - 1 tone,

- disarming - 2 tones,

- clearing alarm - 4 tones,

- denial of arming or arming procedure failure - 7 tones.

The tone duration is approx. 0.3 seconds.

24. MONO Switch - controlled by users, zones or timers. Using a code, zone violation or turning timer on will activate the output for a preprogrammed time.

25. BI Switch - controlled by users, zones or timers. Depending on the current status, using a code or violating a zone will activate/deactivate the output. Turning the timer ON activates the output, and turning the timer OFF deactivates the output.

Note: If the 24. MONO Switch or 25. BI Switch type output is to be controlled from the keypad, it must be assigned to a group of outputs (see: Output groups).

26. Timer - the output controlled by timers.

27. Trouble status - indicates the troubles.

28. AC loss (mainboard) - immediate - indicates the loss of AC power to the control panel mainboard.

29. AC loss (technical zone) - indicates the violations of 59. Technical-AC loss type zones.

30. AC loss (expansion module) - indicates the loss of AC power to the modules with power supply.

31. Battery trouble (mainboard) - indicates the low battery of the control panel mainboard.

32. Battery trouble (technical zone) - indicates the violations of 60. Technical-Battery low type zones.

33. Battery trouble (expansion module) - indicates the low battery of the modules with power supply.

34. Detector trouble - indicates the zone troubles.

35. Telephone line in use status - indicates that the telephone communication is in use.

36. Ground Start - generates a control pulse necessary for work with some types of telephone exchange.

37. Reporting acknowledgement - indicates the acknowledgement of reporting.

38. Service mode status - indicates that the service mode is entered.

39. Test vibration detectors - intended for testing the vibration detectors in one partition (see: 10. 24h Vibration zone type - Zone types). The output cut-off time defines the duration of testing the vibration detectors in the selected partition.

40. Cash machine bypass status - indicates bypassing the 11. 24h Cash machine type zones in partitions with cash dispenser.

41. Power supply - intended for supplying external devices.

42. Power supply on armed - dedicated to powering the detectors which should not be active when the system is disarmed. Gets active when the arming procedure is started (active during the exit delay countdown).

43. Resetable power supply - the power supply output with optional reset by the user. The programmed cut-off time is the time during which the output will be turned off.

44. Fire detectors power supply - intended for supplying the fire detectors with automatic alarm verification. Violating the fire zone will turn the power off (for the time programmed as the output cut-off time) and if another violation occurs after the power is turned on again, the fire alarm will be triggered. The output can be reset by the user.

45. Partition block status - indicates a temporary blocking of the partition armed status. If the output cut-off time is different from 0, the output will signal that the partition blocking is ending (the output will turn on for a programmed time before the blocking ends).

46. Outputs logical AND - active when all the control outputs with normal polarity are active and all the control outputs with reversed polarity are inactive (because of the Pol.+ option, the output can be used for logical negation). See: Logical functions of outputs.

47. Outputs logical OR - active when any control output with normal polarity is active or any control output with reversed polarity is inactive (because of the Pol.+ option, the output can be used for logical negation). See: Logical functions of outputs.

48...63 Voice message 1-16 - activated by the telephone messaging function. It enables any external device to be used for playback of notification messages. When programming the telephone messaging, the number of message to be played back is to be programmed. The messaging will turn on the corresponding output.

64...79 Remote switch 1-16 - intended for control using the telephone (DTMF). The control is available to the users having a telephone code. Additionally, the outputs can be controlled using the user Outs control function.

Notes:

If an output of the Remote switch type is to be controlled from the keypad, it must be assigned to a group of outputs (see: Output groups).

If a cut-off time has been programmed for a Remote switch type output, the output will operate similarly to the 24. MONO Switch type output.

80. No guard tour - indicates lack of guard tour.

81. AC loss (mainboard) - long - indicates the loss of AC power supply to the control panel mainboard, when the trouble lasts long enough to be saved to the event log (see: AC loss report delay parameter - Times).

82. AC loss (expansion module) - long - indicates the loss of AC power supply to the modules with power supply unit, when the trouble lasts long enough to be saved to the event log (the delay is programmed individually in each module).

83. Outputs off - active when all selected outputs are turned off.

84. Access code entering - indicates the entering the user code.

85. Use of access code - indicates the using a code for arming/disarming.

86. Door open indicator - indicates the opening the door supervised by a module executing the access control functions.

87. Door too long opened indicator - indicates the long open door supervised by a module executing the access control functions.

88. Burglary alarm (no fire and tamper) - signals burglary alarms and PANIC alarms from keypads.

89. 50% of log memory filled - informs that 50% of the event log area has been filled since the last event log reading with the DLOADX program.

90. 90% of log memory filled - informs that 90% of the event log area has been filled since the last event log reading with the DLOADX program.

91. Auto-Arm delay start - signals starting the Auto-arming delay countdown for a programmed time period (see: Partitions).

92. Auto-Arm delay status - indicates the Auto-arming delay countdown (see: Partitions).

93. Unauthorized access - signals unauthorized opening of a door monitored by the module executing access control functions.

94. Alarm - Unauthorized access - similarly as type 93, but the signaling only applies to modules with enabled Alarm on unauth. access option.

95. IP reporting trouble - signals troubles related to reporting over Ethernet and by means of GPRS.

96. Telephone line trouble - informs about telephone communication troubles.

97. Voice message - similarly as types 48-63, but the numbers of synthesizers (messages) must be selected.

98. Remote switch - similarly as types 64-79, but the numbers of remote switches must be selected.

99. Access card read - signals read-in of the user card.

100. Card Hold - down - signals holding the user card.

101. Card read - expander - signals that the card has been read in indicated modules/keypads.

Note: The 101. Card read - expander type output may be used for execution of the access control function from INT-KLCDR or INT-KLFR keypad. To do so:

- in the output settings, indicate the keypad on which reading in the card will activate the output, and the partitions from which the users will be able to open the door,

- in the keypad settings, assign the door opening function to presenting / holding the card and indicate the 101. Card read - expander type zone as the door to be opened.

102. Link trouble - wireless zone - signals lack of communication with wireless devices assigned to the selected zones.

103. Link trouble - wireless output - signals lack of communication with wireless devices assigned to the selected outputs.

104. Wireless device - low battery - signals some problems with power supply of wireless devices.

105. Shutter up - dedicated for raising the roll shutters. It becomes active after violation of selected zones or disarming of selected partitions. It can also be triggered from the keypad, by means of the user function Outs control. The cut-off time programmed for the output should be longer than that required for raising the roll shutters.

106. Shutter down - dedicated for lowering the roll shutters. It becomes active after violation of selected zones or arming of selected partitions (upon starting the arming procedure). It can also be triggered from the keypad, by means of the user function Outs control. The cut-off time programmed for the output should be longer than that required for lowering the roll shutters.

Notes:

The roller shutter “up” and “down” functions must be assigned to consecutive (following each other) physical outputs.

If the 105. Shutter up and 106. Shutter down type outputs are to be controlled from the keypad, they must be assigned to a group of outputs (see: Output groups).

For the 105. Shutter up and 106. Shutter down type outputs, indicate a partition so that these outputs can be controlled from the keypad serving the given partition. If the partition status is not to control the output status, enable the Not controlled by arming option.

107. Card on reader A - indicates the proximity card / DALLAS iButton read-in by the expander reader A. It can also signal card reading in the LCD keypad.

108. Card on reader B - indicates the proximity card / DALLAS iButton read-in by the expander reader B. It can also signal card reading in the LCD keypad.

109. Zones logical AND - active, when all zones selected as the control ones are violated.

110. Alarm - not verified - signals unverified alarms.

111. Alarm - verified - signals verified alarms.

112. Verified - no alarm - informs that the alarm has not been verified (during the alarm verification no alarm was triggered by any other zone included in the verification).

113. Verification disabled status - signals disabling alarm verification.

114. Zone test status - indicates the zone testing by means of user functions.

115. Arming type status - active when selected partitions are armed in the selected mode.

116. Internal siren - signals the same alarms and violations as the 1. Burglary or 9. DAY Alarm output type (logic product of the 1. Burglary and 9. Day Alarm outputs).

117. Tampering status - informs about tamper of selected zones, keypads and expanders.

118. Keyfob battery low - informs about low battery in keyfobs belonging to selected users. Refers to the 433 MHz keyfobs (supported by the INT-RX or INT-RX-S modules) or the APT-100 keyfobs (supported by the ABAX system).

119. Wireless system jamming - indicates the jamming of device supporting the ABAX wireless system (ACU-120, ACU-270, ACU-100 or ACU-250 controllers).

120. Thermostat - active when the temperature measured by ATD-100 wireless detectors drops below the specified temperature threshold.

121. Masking - signals for a programmed time masking the detectors connected to the 3EOL zones.

122. Masking status - indicates the masking the detectors connected to the 3EOL zones.

## Logical functions of outputs

It is possible to use any number of outputs as virtual outputs to control the 46. Outputs logical AND or 47. Outputs logical OR type output.

###### Example of using output functions 46 and 47

- Assign functions to the outputs which do not physically exist:

- output 63: function 1. Burglary,

- output 64: function 23. Arm/Disarm beep.

- Program the output 1, to which the siren is connected, as 47. Outputs logical OR, and select the outputs 63 and 64 as the controlling ones. The output 1 will be turned on, if the output 63 or 64 is active.

- Program the output 62, which does not exist physically, as 26. Timer type. Program the timer, which is to control the output, as a daily one, turned on at 16.00 and turned off at 8.00.

- Program the output 2, to which the siren is connected, as 46. Outputs logical AND, and indicate the outputs 1 and 62 as the controlling outputs. As a result, the output 2 will signal alarms and confirmation of partition arming/disarming, but only from 16:00 to 8:00. Beyond these hours, the output will be inactive.

## Output groups

The outputs of MONO switch, BI switch, Remote switch, Shutter up and Shutter down type can be grouped by the function performed by them. Each group may be given a name.

The numbers of fields in the tables correspond to those of outputs. The field color has the following meanings:

white - the output does not belong to the group,

orange - the output belongs to the group.

Double-click on the field to change its color.

Notes:

If all outputs are assigned to one group of outputs, the keypad will not display the list of output groups upon starting the Remote control user function, but it will immediately display the list of outputs which can be controlled.

The output can be assigned to a few groups.

If the output is not assigned to any group, it cannot be controlled from the keypad.

# Timers

The timers enable some functions to be automatically executed by the control panel (arming/disarming, turning on/off devices connected to outputs, etc.). The timer compares the time to that of the control panel clock and executes the selected function at the programmed time.

---------------------------------------------------

No. - timer number.

Name - individual timer name (up to 16 characters).

User edits - if this option is enabled, the users can edit the timer parameters by using the keypad.

Note: Parameters of the timers indicated as the controlling ones for the 120. Thermostat type output can be edited by the user even if the User edits option is disabled.

###### Monday / Tuesday / Wednesday / Thursday / Friday / Saturday / Sunday

Timer parameters for each day of the week.

On - timer starting time. Next to the time, enter an additional digit to define the arming mode which will be activated by the timer: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay.

Off - timer ending time.

###### Everyday

Timer parameters for those days of the week for which no parameters have been programmed.

On - timer starting time. Next to the time, enter an additional digit to define the arming mode which will be activated by the timer: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay.

Off - timer ending time.

###### Exception

The exception is the period during which the timer will be started/ended at a different time. 4 exceptions can be programmed for a timer.

From - the date from which the exception will apply.

To - the date to which the exception will apply.

On - timer starting time. Next to the time, enter an additional digit to define the arming mode which will be activated by the timer: 0 - full arming; 1 - full arming + bypasses; 2 - arming without interior; 3 - arming without interior and without entry delay.

Off - timer ending time.

###### Buttons

Print - click to open Timers settings printout window.

Details - click to open the window with the settings of the selected timer.

OK - click to close the window.

User schedules

## User schedules

The user schedules are defined for the needs of Scheduled type users. You can define up to 8 time schedules.

---------------------------------------------------

Name - individual name of the schedule (up to 16 characters).

Timers - the numbers of fields in the table correspond to those of timers. The field color has the following meanings:

white - the timer has no effect on the schedule,

orange - when the timer is active, the user will have access.

Double-click on the field to change its color.

## Timers settings printout

A table with information about timers are displayed in the window.

-----------------------------------------------------------

Do not print empty/not used items - if the option is enabled, blank table rows will not be printed.

###### Buttons

Print - click to print information about timers.

Cancel - click to close the window.

# Reporting

The control panel can send event codes to the monitoring station using the following transmission paths:

analog telephone line,

Ethernet (connection of the ETHM-1 Plus / ETHM-1 module to the control panel required),

GPRS (INT-GSM module must be installed in the alarm system or SATEL GSM module must be connected to the control panel),

SMS (INT-GSM module is required to be installed in the alarm system) - the control panel gets no acknowledgement of event code receipt.

The control panel will try to send event code to the monitoring station using in turn:

- ETHM-1 Plus / ETHM-1 module and/or INT-GSM module. If several such modules are connected to the control panel, that with the lowest address will be used. Event code can be sent via Ethernet, GPRS or SMS.

Note: When configuring the ETHM-1 Plus module to which the INT-GSM module is connected, or when configuring the INT-GSM module connected directly to the control panel, define priority of the transmission paths. The transmission path which is not included in the list defining the priority of transmission paths, will not be used.

- SATEL GSM module for GPRS transmission.

- analog telephone line (basic and backup telephone number).

If the event code is successfully sent via one transmission path, the other transmission paths will not be used.

If sending the event code via one transmission path fails, the control panel will try to send the event code by using the next transmission path. In the case of reporting via the telephone line, if the event cannot be sent despite completion of the preprogrammed number of retries, the control panel will hang up until a next event occurs, or for a specified period of time. After the time expires, the control panel will make further attempts to send the event.

Monitoring stations

SIA-IP

Identifiers assignment

Event codes

Starting the reporting

## Monitoring stations

Reporting - TELEPHONE - with this option enabled, the control panel can send event codes by means of the telephone line.

Reporting - ETHM - the option is available if the ETHM-1 Plus / ETHM-1 module is connected to the control panel, but the INT-GSM module is not included in the alarm system. If this option is enabled, the control panel can send event codes over Ethernet by using the ETHM-1 Plus / ETHM-1 module.

Reporting - ETHM/INT-GSM - the option is available if the INT-GSM module is installed in the alarm system. If this option is enabled, the control panel can send event codes via Ethernet by using the ETHM-1 Plus / ETHM-1 module and/or via GPRS and SMS by using the INT-GSM module.

Reporting - GPRS - if this option is enabled, the control panel can send event codes via GPRS by using the SATEL GSM module.

Note: The Reporting - GPRS option does not apply to GPRS reporting via the INT-GSM module.

###### Options

Station 1 or 2 - if this option is selected, the control panel will make an attempt to send the event code to station 1 and, if unsuccessful, to station 2.

Station 1 - if this option is selected, the event codes are only sent to station 1.

Station 2 - if this option is selected, the event codes are only sent to station 2.

Station 1 and 2 - if this option is selected, the event codes are sent to both stations. For most formats, it is possible then to define which events will be sent to the given station (see: Events assignment).

Dual path reporting - the option is available when the ETHM-1 Plus module with the INT-GSM module attached to it is connected to the control panel (ETHM+GSM). The control panel will make an attempt to send the event code to station 1 and, if unsuccessful, to station 2.

Note: The dual path reporting requires that the following settings be additionally programmed:

- just one transmission path for Station 1 (Ethernet) (Reporting),

- priority transmission path for Station 2: GPRS SIM1 or GPRS SIM 2 (Reporting),

- IP format for both stations: SIA-IP,

- supervision of the link between the control panel and the central station: Supervision interval parameter configured at least for the first monitoring station (SIA-IP).

No module restart reports - when this option is enabled and the Contact ID or SIA format is used for reporting, no event codes referring to module restarts will be sent to the monitoring station.

Advanced - click to open the Reporting options window.

###### Monitoring station 1 / Monitoring station 2

Reporting format - format in which event codes are sent to the monitoring station.

Note: In the TELIM format, events can only be sent via the analog telephone line.

Telephone

Tel. number - basic telephone number of the monitoring station (see: Programming telephone numbers).

Backup tel.no./format - a backup telephone number of the monitoring station / format in which event codes are sent to the backup telephone number of the monitoring station. The control panel will make an attempt of reporting to that telephone number, if the attempt of reporting to the basic telephone number fails.

Repetitions - the number of attempts to establish telephone connection with the monitoring station after which, if there is no connection (busy number, no answer from the station, etc.), the control panel will suspend reporting. Up to 31 retries can be programmed. Programming the value 0 means that monitoring will be suspended after 8 attempts.

Suspend time - the time for which telephone reporting is suspended, after making the programmed number of attempts to establish connection with the monitoring station. The control panel will resume the attempt of establishing telephone connection with the monitoring station after this time expires or a next, new event occurs. Up to 30 minutes can be programmed. Programming the value 0 means that an attempt to establish telephone connection with the monitoring station will only be taken after occurrence of a new event in the system.

ETHM/GPRS

Server - the address of STAM-2 monitoring station (or SMET-256 converter). It can be entered in the form of IP address (4 decimal numbers separated by dots) or as a name.

Port - the number of port through which communication with the monitoring station will be effected.

Station key - the key with which the data sent to the monitoring station will be encrypted (a string of up to 12 alphanumeric characters). The parameter applies to the IP SATEL format.

IP format - if the event codes are to be sent via Ethernet or GPRS, specify whether SATEL format or SIA-IP format (SIA DC-09 standard) will be used.

Protocol - if the event codes are to be sent via Ethernet or GPRS, specify whether TCP or UDP protocol will be used.

ETHM key - the string of up to 5 alphanumeric characters intended to identify the control panel for the purposes of reporting via Ethernet. The parameter applies to the IP SATEL format.

GPRS key - the string of up to 5 alphanumeric characters intended to identify the control panel for the purposes of reporting using the GPRS technology. The parameter applies to the IP SATEL format.

Note: It is recommended that the maximum number of characters be programmed for the keys and that letters, digits and special characters be used, as this will ensure higher security of the transmission.

Identifiers

Each event code is sent to the monitoring station with an identifier. Up to 8 identifiers plus a system identifier can be programmed. Sent with the system identifier are events related to the alarm system (troubles, tests, etc.).

4 characters (digits or letters from A to F) must be programmed for each identifier. Using the digit 0 in the identifier is not recommended.

For the pulse, Ademco Express, Contact ID (selected) or SIA (selected) formats, you must define which events will be sent with the given identifier (see: Identifiers assignment).

Note: For the Contact ID (full) or SIA (full) formats, each object has its own identifier. Therefore, the identifiers of non-existing objects need not to be programmed. In the system event identifier field, you should re-enter the identifier of the object which is responsible for the system (for example, the object, where the control panel is installed).

SIA prefix / TELIM prefix - 2 characters which will precede each of the identifiers in case of the SIA and TELIM formats. Thus an identifier consisting of 6 characters can be obtained. 2 hexadecimal characters (digits or letters from A to F) can be programmed. Entering 00 means that the prefix will not be added. Using the digit 0 in the prefix is not recommended.

Events assignment

If the events are to be sent to both stations (Station 1 and 2 is selected), you can define which event types will be reported to the given station.

Note: It is not possible to assign events for the Contact ID (full) and SIA (full) formats.

###### Buttons

Import reporting data - click to import reporting data from another alarm system.

Export to STAM - click to export reporting data for purposes of the monitoring station. When saving the file, you can select whether you want to export system names or codes, and for purposes of which monitoring station (STAM-1 or STAM-2).

Print - click to print reporting settings.

OK - click to close the window.

### Reporting options

Long kiss-off signal - with this option enabled, the control panel will accept a long kiss-off (acknowledgment) signal for receiving events in case of Ademco Express and Contact ID formats. Enable this option in the event of telephone reporting if the monitoring station acknowledges receiving events in a non-standard way (the kiss-off signal is longer than 800 ms).

###### Formats DTMF/SIA

Longer waiting for initial handshake - with this option enabled, the control panel will wait longer for handshake from the monitoring station in case of sending events in the Ademco Express, Contact ID or SIA format. Enable this option in the event of telephone reporting, if the monitoring station sends a non-standard initial handshake.

###### SIA options

Identifier confirmation required - if this option is enabled, the control panel waits for acknowledgement by the monitoring station of receiving the identifier with which the data were sent. The option refers to the telephone reporting.

6-character identifier - if this option is enabled, events will be sent with a 6-character identifier. It consists of 2 parts: 2-character prefix and 4-character identifier.

Send event source name - if this option is enabled, the name of event source (zone, user, etc.) will also be sent along with the event code.

Send event partition name - if this option is enabled, the name of partition where the event occurred will also be sent along with the event code.

Each data block conf. required - if this option is enabled, the control panel waits for acknowledgement by the monitoring station of receiving each data block. The option refers to the telephone reporting.

Extended charset - if this option is enabled, not only ASCII characters, but also national characters can be sent.

## SIA-IP

###### Monitoring station 1 / Monitoring station 2

Send MAC address - if this option is enabled, the MAC address of ETHM-1 / ETHM-1 Plus or GSM module will be sent with event code.

Send timestamp - if this option is enabled, the date and time will be sent with event code (the monitoring station can change the date and time in the control panel).

Encrypt data - if this option is enabled, the data to be sent will be encrypted, and the date and time will be sent with event code (the monitoring station can change the date and time in the control panel).

SIA-IP key - the key to encrypt data to be sent using the SIA-IP format.

hex - if the option is enabled, you can enter up to 32 hexadecimal characters as the SIA-IP key. If the option is disabled, you can enter up to 16 alphanumeric characters as the SIA-IP key.

SIA-IP acct - a string of up to 16 hexadecimal characters, which is used to identify the control panel for the purpose of reporting in SIA-IP format.

Supervision interval - an additional transmission can be sent at specified intervals to check communication with the monitoring station. You can program a number of days, hours, minutes and seconds between the transmissions.

## Identifiers assignment

Define the identifier with which events relating to individual partitions, zones, keypads and expansion modules will be sent. If no identifier is assigned to the given element of the system, it will be impossible to define codes for events relating to it.

Notes:

For the Contact ID (full) and SIA (full) formats, you do not have to assign any identifiers.

For the Contact ID (selected) and SIA (selected) formats, identifiers must be assigned to the system components that are to be monitored. These identifiers do not have to be consistent with those of the object. The assignment of identifiers will make it possible to define in the Event codes tab the events that are to be reported, but it will have no effect on the identifier with which the code will be sent.

## Event codes

Note: Prior to programming the event codes, you should assign the identifiers (see: Identifiers assignment).

For the pulse and Ademco Express formats, it is necessary to program codes which will be sent to the monitoring station if the defined events occur. The reported events are those for which a code different from "00" has been programmed. 2 hexadecimal characters (digits or letters from A to F) are to be programmed.

Note: In case of the Contact ID (selected) and SIA (selected) formats, indicate the events which are to be reported, entering for them any code different from “00” (a code consistent with the format specification will be sent, not the entered one). The events for which the “00” code has been programmed will not be reported.

###### Test transmissions

The test transmission may be sent:

at a specified time. The test transmission code will be sent regularly at a defined time. The number of days between transmissions and the time of sending transmission are programmed.

in specified time intervals. For each monitoring station, the number of days, hours and minutes between transmission can be individually programmed. The test transmission code will be sent:

- after a predefined period of time has elapsed since the last transmission, irrespective of whether it was a test transmission, or the code of another event was sent (the No sync. to last transmission option disabled),

- at predefined time intervals (the No sync. to last transmission option enabled).

## Starting the reporting

- Get the data necessary to properly start the reporting from the monitoring station operator:

  - depending on how the events are reported:

- telephone reporting: telephone number of the monitoring station,

- reporting via the ETHM-1 Plus / ETHM-1 / INT-GSM module: server address, TCP port number, Station key and ETHM key,

- GPRS reporting via the SATEL GSM module: server address, TCP port number, Station key and GPRS key.

  - transmission format required by the monitoring station,

  - identifiers assigned to the alarm system,

  - list of event codes (not applicable to Contact ID and SIA formats).

- Determine whether the event codes will be sent to both monitoring stations or to one of them only (enable one of the options: Station 1 or 2, Station 1, Station 2 or Station 1 and 2 - Monitoring Stations).

- For the monitoring station to which event codes are to be sent:

- define the format in which event codes will be sent (Reporting format parameter - Monitoring Stations),

- if you select Ademco Express, Contact ID or SIA format, configure the additional options (Reporting options),

- program the identifiers to be sent with the event codes (Monitoring Stations),

- for the SIA or TELIM format, if the identifier is to consist of 6 characters, program SIA prefix / TELIM prefix (Monitoring Stations).

- If a transmission format other than Contact ID (full) or SIA (full) is selected, program the codes for events which are to be reported:

- assign identifiers to the partitions, zones, keypads and expansion modules (Identifiers assignment),

- program the codes for events which are to be reported (Event codes).

- Define the parameters of test transmissions (Event codes).

Telephone reporting

Ethernet reporting

GPRS reporting

SMS reporting

### Telephone reporting

- Enable the Reporting - TELEPHONE option (Monitoring Stations).

- Configure the telephone options (Telephone):

- determine how the telephone numbers should be dialed (Tone dialing; in case of the pulse dialing option - Pulse 1/1,5 (off 1/2)),

- determine whether the control panel, prior to dialing the number, should check the telephone line for dialing signal (No dial tone test).

- Program the monitoring station parameters (Monitoring Stations):

- phone number,

- the number of attempts to connect to the station after which, if there is no connection, the control panel will suspend reporting,

- time for which reporting will be suspended after the programmed number of attempts to establish connection with the station has been made.

### Ethernet reporting

Notes:

The ETHM-1 / ETHM-1 Plus module must be connected to the control panel.

Events in TELIM format cannot be sent through Ethernet network.

- Enable the Reporting - ETHM / Reporting - ETHM/INT-GSM option (Monitoring Stations).

- Program the monitoring station parameters (Monitoring Stations):

- monitoring station address,

- port.

- Define whether the events are to be sent in SATEL format or SIA-IP format (IP format - Monitoring Stations).

- If the SATEL format is to be used, program (Monitoring Stations):

- data encryption key (Station key),

- control panel identifier for the purposes of Ethernet reporting (ETHM key).

- If the SIA-IP format is to be used, configure the additional options and parameters (SIA-IP).

- Specify whether TCP or UDP protocol is to be used (Monitoring Stations).

- Configure the Ethernet module network settings (ETHM-1 / ETHM+GSM).

- If the INT-GSM module is connected to the ETHM-1 Plus module, define the priority of Ethernet reporting in the ETHM-1 Plus module settings (Reporting).

### GPRS reporting

Note: The TELIM format events cannot be sent using the GPRS technology.

###### Reporting by using the INT-GSM module

- Enable the Reporting - ETHM/INT-GSM option (Monitoring Stations).

- Program the monitoring station parameters (Monitoring Stations):

- monitoring station address,

- port.

- Define whether the events are to be sent in SATEL format or SIA-IP format (IP format - Monitoring Stations).

- If the SATEL format is to be used, program (Monitoring Stations):

- data encryption key (Station key),

- control panel identifier for the purposes of Ethernet reporting (ETHM key).

- If the SIA-IP format is to be used, configure the additional options and parameters (SIA-IP).

- Specify whether TCP or UDP protocol is to be used (Monitoring Stations).

- Configure the GPRS settings of the INT-GSM module (GSM phone [the module connected directly to the control panel] / GSM phone [the module connected to the ETHM-1 Plus module]).

- Define the priority of GPRS reporting in the settings of the module (Reporting [the module connected directly to the control panel] / Reporting [the module connected to the ETHM-1 Plus module]).

###### Reporting by using the GSM module

Note: If the event codes are to be sent via the SATEL GSM module:

- the GSM-X, GSM LT-2 (firmware version 2.14 or newer), GSM-4 (firmware version 4.14 or newer) or GSM-5 module must be connected to the control panel,

- the RS-232 ports of the control panel and the GSM module must be connected (if the GSM module is only connected to the control panel dialer terminals (TIP and RING), the GPRS reporting settings will be ignored),

- the External modem and Modem ISDN/GSM/ETHM options must be enabled in the control panel (Telephone).

Notes:

As an external modem, the following module must be connected to the control panel (the RS-232 ports of control panel and module must be connected):

- GSM LT-2 with firmware 2.11 (or later),

- GSM-4 with firmware 4.11 (or later),

- GSM-5.

If the GSM module is only connected to the control panel dialer terminals (TIP and RING), the GPRS reporting settings will be ignored.

The External modem and Modem ISDN/GSM/ETHM options must be enabled in the control panel (see: Telephone).

The TELIM format events cannot be sent using the GPRS technology.

- Enable the Reporting - GPRS option (Monitoring Stations).

- Program the monitoring station parameters (Monitoring Stations):

- monitoring station address,

- port.

- Define whether the events are to be sent in SATEL format or SIA-IP format (IP format - Monitoring Stations).

- If the SATEL format is to be used (Monitoring Stations):

- data encryption key (Station key),

- control panel identifier for the purposes of GPRS reporting (GPRS key).

- If the SIA-IP format is to be used, configure the additional options and parameters (SIA-IP).

- Specify whether TCP or UDP protocol is to be used (Monitoring Stations).

- Configure the GPRS settings (APN, username, password, DNS server) in the GSM module.

### SMS reporting

Note: The TELIM format events cannot be sent as SMS messages.

- Enable the Reporting - ETHM/INT-GSM option (Monitoring Stations).

- In the settings of the INT-GSM module (Reporting [the module connected directly to the control panel] / Reporting [the module connected to the ETHM-1 Plus module]):

- specify the priority of the SMS reporting,

- program the telephone number to which the SMS messages will be sent,

- configure the SMS message format.

# Messaging

In this window, you can configure notification of the system events by using:

- voice messages. The following must be connected to the control panel:

- the INT-VG module or another voice synthesizer,

- telephone line or SATEL GSM module.

PAGER type text messages, whose content can be programmed (the SATEL GSM modules enable the PAGER messages to be converted into SMS). Connection of telephone line or SATEL GSM module to the control panel is required.

SMS messages, whose content is created automatically, based on descriptions from the control panel event log memory. The INT-GSM module must be installed in the system or the SATEL GSM module must be connected to the control panel (RS-232 ports of control panel and module must be connected).

Note: The required SATEL GSM module:

- GSM-X,

- module with LEON telephone and firmware version:

GSM LT-1: 1.14 or newer,

GSM LT-2: 2.14 or newer,

GSM-4: 4.14 or newer,

GSM-5: 5.14 or newer.

Messaging is performed independently from reporting but reporting has the priority. If in the course of messaging some events occur which must be reported to the monitoring station by the control panel, the messaging will be interrupted. The control panel will resume the messaging function after the event codes are reported to the monitoring station.

Telephone numbers

Events assignment

Clearing

Pager messages

Voice messages

SMS messaging

Starting the voice messaging

## Telephone numbers

Telephone messaging - if this option is enabled, the control panel can send notifications via the telephone network of the occurrence of specific events using voice or text messages defined by the installer.

Double voice message - with this option enabled, the voice message is played back twice during telephone messaging.

Max. redial number for one round - the number of attempts to get through after which the control panel will give up messaging for the current round, if it fails to establish connection (the number is busy).

###### The list of telephone to be notified

Description - telephone name or description (up to 16 characters).

Tel. number - the telephone number to which messaging is effected (see: Programming telephone numbers).

Mode - selection of the messaging type for the given telephone number (0 - voice; 1 - PAGER type 1; 2 - PAGER type 2; 3 - PAGER type 3).

Round count - the number of attempts made by the control panel to notify the selected telephone number about the event, if the message reception has not been acknowledged. If the value 0 is entered, messaging for the indicated telephone number will be disabled.

Any code - with this option enabled, it is possible to acknowledge the voice message reception from the telephone keypad, using any sequence of 4 digits.

Code - 4 digits which, when entered from the telephone keypad, will acknowledge reception of the voice message.

Note: If no code has been programmed to acknowledge receipt of the voice message, nor the Any code option has been enabled, the control panel will recognize receipt of the message as acknowledged when the receiver is picked up after two rings and any sound occurs.

User - if a code has been programmed to acknowledge receipt of the voice message or the Any code option has been enabled, a user can be assigned to the telephone. Thus, if the INT-VG module is connected to the control panel, the user will be automatically granted access to the voice menu after acknowledgement of the voice messaging.

## Events assignment

Available in the tab is a list of all events the control panel will notify about. If the control panel is to notify about a given event, proceed as follows:

- enter in the Voice message column the number of voice message which is to be played back in case of voice messaging,

- enter in the Pager message column the number of message which is to be sent in case of PAGER or SMS messaging,

- in columns designated by numbers (the numbers correspond to telephone numbers), define whether the given telephone is to be notified:

X - yes,

blank field - no.

Double-click on the field to make changes.

## Clearing

###### Partitions

For each telephone number, you can indicate the partitions in which alarm clearing will clear notification about that alarm (the messages will not be sent to that telephone number, but can be sent to other numbers). The numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - alarm clearing will have no effect on notification,

orange - alarm clearing will clear notification.

Double-click on the field to change its color.

Note: Messaging in partitions can be cleared irrespective of the Clear messaging on alarm clearing option (see: Other).

###### Acknowledged

Acknowledgement of receiving a voice message by one of the telephones may cancel messaging to the other telephones. The numbers of fields in the table correspond to those of telephones. The field color has the following meanings:

white - acknowledgement of receiving voice message has no effect on messaging to this telephone,

orange - acknowledgement of receiving voice message cancels messaging to this telephone.

Double-click on the field to change its color.

## Pager messages

No. - number of text message.

Pager message / SMS - the content of the message which will be used for PAGER or SMS type of messaging.

###### Message type

Select the type of message editing:

Digital - for messages to be sent to PAGER call systems.

Text - for messages to be sent as SMS messages.

###### Buttons

Pager type - click to open Pager types window.

### Pager types

For messaging using the PAGER type messages, you must define the parameters of pager identification. Default parameters of the pager type 1 are adjusted to the SATEL GSM module requirements for conversion of the PAGER type message into SMS message.

## Voice messages

In the tab you can enter the content of voice messages used for notification.

## SMS messaging

The settings described below apply to SMS messaging via the SATEL GSM module. The settings are not available, when the INT-GSM module is installed in the alarm system.

The settings for SMS messaging via the INT-GSM module you can configure in the module settings (SMS messaging / CLIP control [the module connected directly to the control panel] / SMS messaging / CLIP control [the module connected to the ETHM-1 Plus module]).

SMS messaging - if this option is enabled, the control panel can send event notifications by using SMS messages whose content is created automatically, based on the control panel event log. The SATEL GSM module must be connected to the control panel.

###### The list of telephone to be notified

Name - telephone name or description (up to 16 characters).

Tel. number - the telephone number to which messaging is effected (see: Programming telephone numbers).

ON - define whether the given telephone is to be notified:

X - yes,

blank field - no.

Double-click on the field to make changes.

Events type - define whether the given telephone is to be notified of events of the given type:

X - yes,

blank field - no.

Double-click on the field to make changes.

Part. - define whether the given telephone is to be notified of events in the given partition:

X - yes,

blank field - no.

Double-click on the field to make changes.

## Starting the voice messaging

- Enable the Telephone messaging option (Telephone numbers).

- Configure the telephone options (Telephone):

- determine how the telephone numbers should be dialed (Tone dialing; in case of the pulse dialing option - Pulse 1/1,5 (off 1/2)),

- determine whether the control panel, prior to dialing the number, should check the telephone line for dialing signal (No dial tone test),

- determine whether the control panel is to play back the voice message after going off-hook, or 15 seconds after the dialing is completed (No answer test),

- determine whether the voice message is to be played back once or twice (Double voice message).

- Define the number of attempts to get connected in one round (function Max. redial number for one round - Telephone numbers).

- Configure the settings of the telephones that are to be notified (Telephone numbers):

- enter the telephone numbers,

- in the Mode column enter 0,

- define the number of attempts made by the control panel to notify the telephone about the event, if receipt of the message has not been acknowledged,

- define how the receipt of voice message is to be acknowledged (if the messaging is to be acknowledged, enable the Any code option or enter the 4-digit code),

- in the User column enter the user number, if the telephone user is to automatically get access to the INT-VG module voice menu after entering the code.

- Assign the numbers of voice messages to events (Events assignment).

- Specify which telephones are to be notified about specific events (Events assignment).

- In order to limit unnecessary messaging, define the cases in which notification can be cleared (Clearing).

- Record or synthesize the voice messages which are to be used for messaging by INT-VG module or CA-64 SM expander.

# E-mail messaging

E-mail messaging - if this option is enabled, the control panel can send event notifications by e-mail messages, the content of which is created automatically, based on descriptions from the control panel event log. The ETHM-1 Plus or INT-GSM module must be connected to the control panel.

###### List of e-mail addresses

Email address - e-mail address to which event notifications will be sent.

Note: Because the message is sent to many recipients, the addressees are hidden. If you want the addressee to be shown, place @ before the email address (e.g. @j.smith@example.com).

ON - define whether the given e-mail address is to be notified:

X - yes,

blank field - no.

Double-click on the field to make changes.

Events type - define whether the given e-mail address is to be notified of events of the given type:

X - yes,

blank field - no.

Double-click on the field to make changes.

Part. - define whether the given e-mail address is to be notified of events in the given partition:

X - yes,

blank field - no.

Double-click on the field to make changes.

Mail server

## Mail server

Note: It is required to have an e-mail account so as to enter its parameters in the DLOADX program for the purpose of e-mail messaging.

Mail server (SMTP) - address of outgoing mail server.

Server port - number of outgoing mail port.

User name - name of the mail account used for authentication by the SMTP server (mail account login).

Password - password used for authentication by the SMTP server.

Encryption - you can specify whether and how the outgoing mail is to be encrypted:

none - outgoing mail will not be encrypted.

STARTTLS - outgoing mail will be encrypted using the STARTTLS protocol.

SSL/TLS - outgoing mail will be encrypted using the SSL/TLS protocol.

Do not report SMTP server connection trouble - if this option is enabled, the failure sending e-mail will not trigger any trouble signal.

Subject - subject of the e-mail message. It will be inserted in each e-mail to be sent.

Sender address - e-mail address which will be inserted in the outgoing e-mail message as the sender address. If this field is blank, the name of e-mail account will be treated as the sender address.

###### Buttons

Test - click to send test e-mail message.

OK - click to close the window.

# Answering and remote control

Answering - audio - with this option enabled, the control panel will carry out the function of call answering.

Rings before answer - number of rings after which the control panel will go off hook.

Double call - with this option enabled, the control panel must be called twice for the modem communication to be established. The first time you must wait for the preprogrammed number of rings and hang up. Then you must call back within three minutes and the control panel will answer the call immediately. This solution makes it possible to connect after the control panel some additional devices which will be activated after a preset number of rings (e.g. answering machine, fax, etc.).

Remote control - with this option enabled, the control panel allows the users having a telephone code to operate the Remote switch outputs by using a phone. The option is available if the Answering - audio is enabled.

Answer if all chosen partitions are armed - you can limit operation of the answering and remote control features to the periods when the partitions are armed. The numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - status of those partitions has no effect on availability of the answering and remote control features,

orange - when those partitions are armed, the answering and remote control features are available (all the selected partitions must be armed).

Double-click on the field to change its color.

Note: If the Answering - modem option is enabled (see: Telephone), the control panel will be answering the calls whether the partitions are armed or not.

###### List of users

The table presents the following information about the users:

- name,

- object in which the user has been created,

- list of partitions to which the user has access.

Click on a user to display a list of Remote switch type outputs, which can be controlled by the user (click to select/deselect output).

Activation of the phone calls answering

Activation of the remote control

## Activation of the phone calls answering

- Enable the Answering - audio option.

- Define the rules of call answering by the control panel (Rings before answer parameter and Double call option).

- Define whether the function is to be available at all times, or only when selected partitions are armed (function Answer if partitions are armed parameter).

- Program the telephone codes for the users who are to use the function (see: Users).

## Activation of the remote control

- Activate the call answering function (see: Activation of the phone calls answering).

- Enable the Remote control option.

- Program the selected outputs as the Remote switch.

- Assign the Remote switch type outputs to the users who are to use the function.

# Service note

Using the service note you can communicate with the system users. The service note is displayed on all keypads.

Note: The service note can be edited when the DLOADX program is communicating with the control panel.

---------------------------------------------------

Message to be displayed - service note content (up to 28 characters - 16 in first line and 12 in second).

Display - select on of options:

constant - the note will be displayed without time limit,

do not show - the note will not be displayed,

for - the note will be displayed for a defined number of days (define the number of days in the field on the right).

When - select from when the note is to be displayed:

from - the note will be displayed from the specified day (enter the date in the field on the right: day-month),

instantly - the note will be displayed from saving the changes into the control panel.

Note for - define how the note is to be displayed:

do not show - will not be displayed,

[user name] - will be displayed after entering code by the given user,

[administrator name] - will be displayed after entering code by the given administrator,

user of partition x [x - partition number] - will be displayed after entering code by the user who has access to the given partition,

each Master User - will be displayed after entering code by any administrator,

everyone - will be displayed after entering code by any administrator or user,

always visible - is displayed when no menu or message is displayed (not applicable to virtual keypads),

always visible with sound signal - is displayed when no menu or message is displayed, and the keypad is signaling by two short beeps that menu or message is displayed (not applicable to virtual keypads).

Note cleared by - define how the note is to be cleared:

not erasable - the note cannot be cleared,

[user name] - the note can be cleared by the given user,

[administrator name] - the note can be cleared by the given administrator,

user of partition x [x - partition number] - the note can be cleared by the users who have access to the given partition,

each Master User - the note can be cleared by any administrator,

everyone - the note can be cleared by any administrator or user.

###### Buttons

Save - click to write the changes to the control panel (the changes cannot be written using buttons in the main menu).

Close - click to close the window.

# Users

Note: Editing users of the given object is possible, if the Serv. can edit option is enabled by the administrator of this object.

The data about administrators and users are presented in the table.

Owner - information on who has created and can remove the given user from the system:

S - service technician (installer). The service technician is owner of all administrators, i.e. can add them to or remove from the system. If the service technician has added a user, the owner of such user will be the administrator of the given object.

A1, A2 … - administrator of the given object (A1 - administrator of object 1, A2 - administrator of object 2, etc.). The administrator can edit and remove all users of his partition.

U1, U2 … - user, who has created the given user.

P - number of the object to which the given user belongs. Click on the column heading to change the way of data sorting in the table (the users are sorted by objects, or not).

No. - user number. Click on the column heading to sort users in the table by their number.

User name - individual user name (up to 16 characters). Click on the column heading to sort users in the table by their name.

Type - user type (see: User types).

Time - additional parameter for some types of users:

- validity for the Renewable and Temporary type of user;

- time schedule (first number) and validity (second number) for the Scheduled type of user.

Code - a string of 4 to 8 digits for authorization of the user when using keypads and code locks. The codes are presented as a sequence of asterisks, unless the Show codes option is enabled. If the code is presented against yellow background, it means that another user has accidentally entered this code during code changing, and, therefore, it must be changed.

Tel. code - a string of 4 digits for authorization of the user when using the functions of telephone call answering and telephone control.

Part. - numbers of partitions to which the user has access. To select the partitions, use the Part./keypads tab on the right side of the window.

Keyp./reader - addresses of partition keypads, code locks, proximity card reader expanders and DALLAS chip expanders, to which the user has access. To select the partitions, use the Part./keypads tab on the right side of the window.

Authority level - numbers of user rights. To select the right, use the Authority level tab on the right side of the window.

Card - code of the user's proximity card.

DALLAS - code of the user's DALLAS iButton.

---------------------------------------------------

Show codes - if the option is enabled, codes of the users who have not changed their codes are shown in the Code column.

###### Information

The tab makes it possible to assign a picture to the user and enter some extra information.

###### Part./keypads

Part. - list of partitions in the system. Select the partitions to which the user is to have access. The numbers of selected partitions are presented in the Part. column.

Keypads/readers - list of partition keypads, code locks, proximity card reader expanders and DALLAS iButtons expanders in the system. Select the modules to which the user is to have access. The addresses of selected modules are presented in the Keyp./reader column.

###### Authority level

A list of all rights is presented in the tab. Select which rights the user is to have. The numbers of selected rights are presented in the Authority level column.

---------------------------------------------------

Arming - the user can arm the system.

Disarming - the user can disarm the system.

Disarm, when other user arm - the user can disarm, if other user has armed (if the user does not have this right, he can only disarm if he has armed).

Partition alarm clearing - the user can clear alarms in partitions to which he has access.

Object alarm clearing - the user can clear alarms in the object to which he belongs.

Other objects alarm clearing - the user can clear alarms in other objects.

Tel. messaging canceling - the user can cancel telephone messaging.

Auto-arming defer - the user can defer arming by the timer.

First code for two codes part. - the user can enter the first code, if 2 codes are needed to arm / disarm.

Second code for two codes part. - the user can enter the second code, if 2 codes are needed to arm / disarm.

Access temporary blocked part. - the user can disarm temporary blocked partitions (With temporary blocking type partition - see: Partitions).

Change access code - the user can change own access code.

Users editing - the user can add, edit and delete users.

Zones bypassing - the user can inhibit the zones.

Zone isolation - the user can isolate the zones.

Clock setting - the user can program the control panel clock.

Trouble state checking - the user can view the current troubles.

Event log reviewing - the user can view the event log.

Detectors resetting - the user can reset the 43. Resetable power supply type outputs (the user has access to Reset zones user function).

Options programming - the user has access to the user functions in the Change options submenu.

Access to menu TEST - the user has access to the user functions in the Tests submenu.

Downloading starting - the user can initiate remote programming of the control panel from the keypad..

Access to BI & MONO outputs - the user can control the outputs.

System state review in GUARDX - the user can use the GUARDX program to operate the system.

Resetting outputs - the user can clear latched outputs (the user has access to Clr.latch.outs user function).

Simple user - having entered the code, confirmed with the # key, the user never selects the partitions which are to be armed / disarmed. All partitions the user has access will be armed / disarmed.

Administrator - the user has access to the menu functions which are reserved for the administrator.

###### Buttons

Add Administrator - click to add new administrator (see: Adding administrator).

Add users - click to add new users (see: Adding user).

Delete - click to remove selected administrator or user (see: Removing administrator/user).

Restore - click to restore selected user settings according to settings in control panel.

Card - click to add a proximity card to the user (see: Adding proximity card).

Dallas - click to add a DALLAS iButton to the user (see: Adding DALLAS iButton).

Print - click to print the user related information.

Export - click to export the user related information to the CSV file.

Close - click to close the window.

Adding administrator

Adding user

Removing administrator/user

Adding proximity card

Removing proximity card

Adding DALLAS iButton

Removing DALLAS iButton

## User types

Normal - basic type of user.

One-time - the user will get one-time access.

Renewable - the user has access to the system for a defined period of time. The user validity time should be entered in the Time column. Before the validity time expires, the control panel will prompt the user to change the code. After the code has been changed, the validity time will run from the beginning.

Temporary - the user has access to the system for a defined period of time. The user validity time should be entered in the Time column. After the validity time expires, the user will have no access to the system.

DURESS - code to be used in hold-up and duress situations. Use it to trigger a silent alarm and send the event code to the monitoring station.

“Mono” output operating - code for control of the MONO switch type outputs.

“Bi” output operating - code for control of the BI switch type outputs.

Blocking partition - the code enables access to the armed partitions. Using the code will block the armed partition(s) (the partition zones will not trigger the burglary alarm). The blocking time is defined individually for each user within the range from 1 to 109 minutes. If, however, the time of bypassing for guard round is defined for the partition and its duration is longer, the blocking will last longer.

Cash machine zones bypassing - the code to be used to unblock access to the cash dispenser (the 24H Cash machine type zones will be temporarily bypassed in the partition).

Guard - using this code means having made the round (additionally, it can result in the partition being temporarily bypassed for the duration of guard round). The installer defines the modules which are used to confirm making the round and determines the time interval between successive rounds. If such a user is granted access to the partition, he/she will have the same possibilities as the Normal type user.

Scheduled - the user has access to the system for a defined period of time, according to a time schedule. The schedule number (use the Timers window, Users schedules tab, to define the time schedule) and user validity time are defined in the Time column.

## Adding administrator

Note: If, at the moment of adding an administrator, the object he is to manage does not exist, it will be automatically created.

- Click on the Add Administrator button. The new administrator will appear in the table.

- Enter individual name of the new administrator.

- Enter a new code instead of the default factory code.

- Click on the Authority level tab and define the authority level of the new administrator.

- Click on the , to write the changes to the control panel.

## Adding user

- Click on the Add users button. The Create users window will open.

- Define in the Users count field how many users are to be added to the system.

Note: Click on the Import from file button to load the text file with a list of the names of users who are to be created (this will load the first 16 characters from each line, excluding the initial blank spaces and digits).

- In the Object field, select in which object the new user is / the new users are to be created.

- In the User settings as field, select on the basis of settings of which user of that object the new user / new users will be created.

- Define how the code of the new user(s) is to be created. The code can be created on the basis of user number, random generated or entered manually.

- Click on the OK button. The new user(s) will appear in the table.

- Enter individual name of the new user(s).

- In the Type column, select the user type.

- If the Renewable, Temporary or Scheduled user type is selected, define additional parameters in the Time column.

- If the code has not been generated automatically, enter it in the Code column.

- If the user is to use the answering and remote control functions, enter the telephone code.

- Click on Part./keypads tab and define to which partitions and modules the user is to have access (by default, the new user is granted access to all existing partitions and identified modules).

- Click on the Authority level tab and define the authority level of the new user.

- Click on the , to write the changes to the control panel.

## Removing administrator/user

- Click on the administrator / user you want to remove.

- Click on the Delete button. The Confirm window will open.

- Click on the Yes button. The Confirm window will close and the administrator / user will be removed from the table.

- Click on the , to write the changes to the control panel.

## Adding proximity card

You can add a proximity card by entering its number manually or reading its number by means of a device provided with proximity card reader.

###### Entering the number manually

- In the Card column, click on the field of the user to whom you want to add a card.

- Enter the card number and confirm by pressing ENTER.

- Click on the , to write the changes to the control panel.

###### Reading the number

- Click on any field related to the user to whom you want to add a proximity card.

- Click on the Card button. The card adding window will open.

- In the Reader field select the device (keypad with built-in reader, proximity card arm/disarm device, expander for proximity card reader etc.) to be used for reading the card number.

- Click on the Add card button.

- According to the prompts displayed in the window, present the card twice to the proximity card reader.

- When the Card read message is displayed, click on the Close button. The card adding window will be closed. The new card number will be displayed in the Card column.

- Click on the , to write the changes to the control panel.

## Removing proximity card

- In the Card column, double click on the field of the user whose card you want to remove.

- Press the DELETE key to clear the card number.

- Click on the , to write the changes to the control panel.

## Adding DALLAS iButton

You can add a DALLAS iButton by entering its number manually or reading its number by means of a DALLAS iButton reader.

###### Entering the number manually

- In the Dallas column, click on the field of the user to whom you want to add an iButton.

- Enter the iButton number and confirm by pressing ENTER.

- Click on the , to write the changes to the control panel.

###### Reading the number

- Click on any field related to the user to whom you want to add an iButton.

- Click on the Dallas button. The iButton adding window will open.

- In the Reader field select the expander for DALLAS iButton readers to be used for reading the iButton number.

- Click on the Add dallas button.

- According to the prompts displayed in the window, read in the iButton twice.

- When the Dallas read message is displayed, click on the Close button. The iButton adding window will be closed. The new iButton number will be displayed in the Dallas column.

- Click on the , to write the changes to the control panel.

## Removing DALLAS iButton

- In the Dallas column, double click on the field of the user whose iButton you want to remove.

- Press the DELETE key to clear the iButton number.

- Click on the , to write the changes to the control panel.

# Keyfobs INT-RX

At the top of the window, the following information on the INT-RX-S / INT-RX expansion modules connected to the control panel is displayed:

- number of the expansion modules bus to which the module is connected,

- expander address,

- expander name,

- version of module firmware (after reading data from the modules).

Before making any changes, click on the Read button, and after making the changes - on the Write button. The data relating to the keyfobs are stored in the expansion modules and are not read / written when you click on the  /  button in the main menu. The data are read only from the lowest address module, but written to all modules.

After clicking on the Read button, if the program will establish communication with the module, information on the module will be displayed against green background.

###### Keyfob information table

The user can have one 433 MHz keyfob. The keyfob is supported by all INT-RX-S / INT-RX expansion modules connected to the control panel.

Notes:

After INT-RX-S / INT-RX expansion module containing the keyfob data is connected to the control panel, keyfobs will be automatically assigned to the existing users. The rule does not apply if it is another INT-RX-S / INT-RX expansion module in the system.

When connecting another INT-RX-S / INT-RX expansion module to the system:

- it should have a higher address than the INT-RX-S / INT-RX expansion modules already connected to the control panel,

- click on the Write button immediately after reading the keyfob data - all the keyfob data will be written to the expansion modules, and thus the data will be the same in all expansion modules.

-----------------------------------------------------------

User name - administrator/user number and name.

S/N - serial number of the 433 MHz keyfob.

Keyfob buttons / zones - number of the zone that will be violated, when the given button or combination of keyfob buttons is pressed. The zone should not exist physically and the wiring type programmed for it must be different from No detector and Follow output. You can program any zone type. You can also define in the field whether pressing the button / combination of buttons is to save the event into control panel memory:

( - event is not to be saved,

no symbol - event is to be saved.

Press the SPACE key to disable/enable generating events using the button.

###### Buttons

Read - click to read the data from the expansion module (the program will only read data from the lowest address expansion module).

Write - click to write the data to the expansion modules. If communication with one of the INT-RX-S / INT-RX modules is lost, writing the keyfob data will not be possible to any module.

New - click to add a keyfob (see: Adding 433 MHz keyfob).

Delete - click to remove a keyfob (see: Removing 433 MHz keyfob).

OK - click to close the window.

## Adding 433 MHz keyfob

You can add the keyfob by entering its serial number manually or reading the serial number during transmission which is sent after the button is pressed.

###### Entering the serial number manually

- Click on the Read button to read the data related to keyfobs.

- Click on the field in the S/N column next to the name of the user to whom you want to assign a keyfob.

- Enter the keyfob serial number and confirm by pressing ENTER.

- Enter the numbers of zones which are to be controlled by individual buttons or combinations of buttons.

- Click on the Write button to write the new keyfob data to the expansion modules.

###### Reading the serial number during transmission

- Click on the Read button to read the data related to keyfobs.

- Click on the field in the S/N column next to the name of the user to whom you want to assign a keyfob.

- Click on the New button. The New window will open.

- According to the command which will appear in the window, press the keyfob button.

- When the keyfob serial number is displayed in the window, click on the OK button. The New window will close. The serial number of the new keyfob will be shown in the S/N column.

- Enter the numbers of zones which are to be controlled by individual buttons or combinations of buttons.

- Click on the Write button to write the new keyfob data to the expansion modules.

## Removing 433 MHz keyfob

Note: Removal of a keyfob will not erase its settings (dependences between the buttons and zones). When added to the user, the new keyfob will have the same settings as the deleted one.

- Click on the Read button to read the data related to keyfobs.

- Click on the field in S/N column next to the name of user whose keyfob is to be removed.

- Click on the Delete button.

- In the window which will be displayed, click on the Yes button to confirm that you want to remove the keyfob. The window will be closed, and the keyfob serial number displayed in the S/N column will be cleared.

- Click on the Write button to save the changes to the expansion modules.

# Keyfobs ABAX

At the top of the window, the following information on the ABAX system controllers connected to the control panel is displayed:

- number of the expansion modules bus to which the controller is connected,

- controller address;

- controller name;

- version of controller firmware (after reading data from the controllers).

Before making any changes, click on the Read button, and after making the changes - on the Write button. The data relating to the keyfobs are stored in the controllers and are not read / written when you click on the  /  button in the main menu. The data are read only from the lowest address controller, but written to all controllers.

After clicking on the Read button, if the program will establish communication with the controller, information on the controller will be displayed against green background.

###### Keyfob information table

The user can have one ABAX keyfob. The keyfob is supported by all ABAX system controllers connected to the control panel.

Notes:

After controller containing the keyfob data is connected to the control panel, keyfobs will be automatically assigned to the existing users. The rule does not apply if it is another controller in the system.

When connecting another ABAX system controller to the control panel:

- it should have a higher address as compared to the controllers already connected to the control panel,

- click on the Write button immediately after reading the keyfob data - all the keyfob data will be written to the controllers, and thus the data will be the same in all controllers.

-----------------------------------------------------------

User name - administrator/user number and name.

S/N - serial number of the ABAX keyfob.

Keyfob buttons / zones - number of the zone that will be violated when the given button or combination of buttons is pressed on the keyfob. The zone should not exist physically and the wiring type programmed for it must be different from No detector and Follow output. You can program any zone type. You can also define in the field whether pressing the button / combination of buttons is to save the event into control panel memory:

( - event is not to be saved,

no symbol - event is to be saved.

Press the SPACE key to disable/enable generating events using the button.

LED - in this field, you can enter up to 3 digits, each of them corresponding to the field number from the list of outputs used for confirmation on the right side of the window. The digits can be from the 1 to 8 range. If you press any keyfob button, the status of three selected outputs will be presented for a few seconds on the LEDs of APT-100 keyfob. This confirms performance of a function or provides information on the current state of the system.

###### Confirmation output selection

Up to 8 alarm system outputs can be used for confirmation. Indicate in each field the output whose status will be sent to the ABAX system keyfobs. Enter the number of field in the LED column, if status of the output selected in this field is to be sent to the keyfob of the given user.

###### Buttons

Read - click to read the data from the controller (the program will only read data from the lowest address controller).

Write - click to write the data to the controllers. If communication with one of the controllers is lost, writing the keyfob data will not be possible to any controller.

New - click to add a keyfob (see: Adding ABAX keyfob).

Delete - click to remove a keyfob (see: Removing ABAX keyfob).

OK - click to close the window.

## Adding ABAX keyfob

You can add the keyfob by entering its serial number manually or reading the serial number during transmission which is sent after the button is pressed.

###### Entering the serial number manually

- Click on the Read button to read the data related to keyfobs.

- Click on the field in the S/N column next to the name of the user to whom you want to assign a keyfob.

- Enter the keyfob serial number and confirm by pressing ENTER.

- Enter the numbers of zones to be controlled by individual buttons or combinations of buttons.

- In the LED column, define the rules of acknowledgement on the LEDs.

- Click on the Write button to write the new keyfob data to the controllers.

###### Reading the serial number during transmission

- Click on the Read button to read the data related to keyfobs.

- Click on the field in the S/N column next to the name of the user to whom you want to assign a keyfob.

- Click on the New button. The New window will open.

- According to the command which will appear in the window, press the keyfob button.

- When the keyfob serial number is displayed in the window, click on the OK button. The New window will close. The serial number of the new keyfob will be shown in the S/N column.

- Enter the numbers of zones to be controlled by individual buttons or combinations of buttons.

- In the LED column, define the rules of acknowledgement on the LEDs.

- Click on the Write button to write the new keyfob data to the controllers.

## Removing ABAX keyfob

Note: Removal of a keyfob will not erase its settings (dependences between the buttons and zones, confirmation rules, etc.). When added to the user, the new keyfob will have the same settings as the deleted one.

- Click on the Read button to read the data related to keyfobs.

- Click on the field in S/N column next to the name of user whose keyfob is to be removed.

- Click on the Delete button.

- In the window which will be displayed, click on the Yes button to confirm that you want to remove the keyfob. The window will be closed, and the keyfob serial number displayed in the S/N column will be cleared.

- Click on the Write button to save the changes to the controllers.

# Data comparison

Presented in the window is information on differences between the computer data and those recently read from the alarm control panel.

###### Buttons

Undo change - click to undo the selected change (settings read out from the control panel will be restored).

Undo all changes - click to undo all changes (all settings read out from the control panel will be restored).

Refresh - click to refresh the list of differences. If the window is open, the list of differences will be refreshed automatically every 2 seconds.

Close - click to close the window.

# Event log

Presented in the window is a list of alarm system events.

No. - number of event in the list.

Date - date of event occurrence.

Time - time of event occurrence.

Event - description of event.

Details - additional information on the event, e.g. name of the partition, zone, user, etc., to which the event refers.

O - object number.

P/K - partition number, module address or output number (for the events providing information about output trouble).

Z/M/U - number of zone, module or user.

S1 S2 - reporting status (S1 - monitoring station 1, S2 - monitoring station 2):

no symbol - the event is not reported.

+ - event successfully reported to the monitoring station.

. - event waiting to be reported to the monitoring station.

! - event not reported yet because of failure of communication with the station (the station does not confirm receiving this information).

Code - internal code assigned to an event in the control panel (consistent with the Contact ID format code for events that are reported in this format).

Note: If, since the last readout, the number of events has exceeded the capacity of control panel memory, part of the older events will be erased. In such a case, a message about lack of continuity of the event log will be displayed in the window.

-----------------------------------------------

Choose - click to open the Choose window.

Print - click to open the Print window.

Refresh - click to refresh the event log (new events are read).

Colored list - with this field selected, the events will be displayed in color (the colors assigned to various event types are presented in the Choose window).

Font - click to open the Font window, where you can set parameters of the font used for event presentation.

Grade2 events - click to open the Grade2 events window.

Close - click to close the window.

## Choose

The window enables the user to select events which are presented in the Event log window. The events can be filtered according to the following criteria:

Events type - types of events that are to be displayed (the event types are highlighted in color, if the Colored list field has been selected in the Event log window).

Range - the range of displayed events can be limited to the selected objects or partitions:

Objects - events will be filtered by objects. The numbers of fields in the table correspond to those of objects. The field color has the following meanings:

white - events from the object will not be displayed,

orange - events from the object will be displayed.

Double-click on the field to change its color.

Note: If no object is highlighted (all fields remain white), events from all objects will be displayed.

Partitions - events will be filtered by partitions. The numbers of fields in the table correspond to those of partitions. The field color has the following meanings:

white - events from the partition will not be displayed,

orange - events from the partition will be displayed.

Double-click on the field to change its color.

Note: If no partition is highlighted (all fields remain white), events from all partitions will be displayed.

From - you can define a date in this field, if events that occurred after this date are to be displayed.

To - you can define a date in this field, if events that occurred before this date are to be displayed.

Only including text - you can define the text that must be included in event description for the event to be displayed.

And including text - you can define the text that, if included in the event description, will cause the event to be displayed next to the events that have been selected by other criteria (event type, range, etc.).

Without including text - you can define the text that, if included in the event description, will cause the event not to be displayed.

###### Buttons

All - click on the button to close the window and display all events in the Event log window (without taking into account the criteria defined in the Choose window).

Choose - click on the button to close the window and display events in the Event log window according to the criteria defined in the Choose window.

Cancel - click on the button to cancel the event selection and close the window.

## Print

The window allows you to define parameters of a printout containing the event log.

Printer - in this field, information on the selected printer is displayed.

Events - the field displays information on events to be printed. The printout contains events currently displayed in the Event log or Grade2 events window.

Printout with reporting status - select this field to include reporting status information in the printout.

Print to text file - with this field selected, the event log will be exported to a text file instead of a printout.

Range - you can define a printout range.

###### Buttons

Properties - click to change a printer.

Print - click to print / export to file the event log.

Cancel - click to close the window.

## Grade2 events

The window displays events required by the EN 50131 standard for Grade 3. The event types are highlighted in color, if the Colored list field has been selected in the Event log window.

No. - number of event in the list.

Date - date of event occurrence.

Time - time of event occurrence.

Event - description of event.

Details - additional information on the event, e.g. name of the partition, zone, user, etc., to which the event refers.

O - object number.

P/K - partition number, module address or output number (for the events providing information about output trouble).

Z/M/U - number of zone, module or user.

Code - internal code assigned to an event in the control panel (consistent with the Contact ID format code for events that are reported in this format).

###### Buttons

Print - click to open the Print window.

Refresh - click to refresh the event log (new events are read).

Close - click to close the window.

# System state

Keypad

Partitions state

Zones state

Outputs, timers, tampers, doors

Troubles

Module power supply

Wireless devices

## Keypad

The keypad displayed on screen is a fully functional keypad. It can be used to operate the control panel in the same way as the LCD keypad connected to the control panel.

Note: Operation of the system from the virtual keypad is available when the program is communicating with the control panel.

## Partitions state

Presented in the window is information on the status of partitions of the alarm system with which the program is currently communicating. The window data are automatically updated.

## Zones state

The window presents information on the status of zones of the alarm system with which the program is currently communicating. Move the cursor over the zone number to display additional information about that zone at the window bottom. The window data are automatically updated.

## Outputs, timers, tampers, doors

Presented in the window is information on the status of outputs, timers, tampers and doors of the alarm system with which the program is currently communicating. The window data are automatically updated.

###### Outputs

You can select whether output activity status (active/inactive) or output voltage (0 V/+12 V) is to be indicated. Depending on your selection:

- the green color means that the output is inactive or the output voltage is 0 V;

- the red color means that the output is active or the output voltage is +12 V.

The gray color indicates that the output is not in the system.

Move the cursor over the output number to present additional information on the output at the bottom of the window.

###### Timers

The status of all system timers is presented (even if they are not programmed). The green color indicates that the timer is disabled, and the red color that it is enabled. Move the cursor over the timer number to present additional information on the timer at the bottom of the window.

###### Tamper

Information on tampers, if any, of the devices connected to the control panel communication buses is presented as follows:

- green color - no tamper;

- red color - tamper (open tamper contact, no tamper contact or verification error);

- gray color - no device at this address.

Move the cursor over the device address to present additional information on the device at the bottom of the window.

###### Door

Presented here is information on the doors supervised by access control modules (partition keypads, code locks, proximity card reader expanders and DALLAS chip reader expanders):

- green color - door closed;

- red color - door open;

- gray color - no door status supervising module at this address.

Move the cursor over the address of door supervising module to present additional information on the module at the bottom of the window.

## Troubles

The window presents information on the troubles in the alarm system with which the program is currently communicating.

Clear trouble memory - the button is available, if the Trouble memory until review option is enabled in the control panel (see: Other). You can use it to reset the trouble memory.

## Module power supply

The window displays real-time information about the power supply of modules connected to the control panel communication buses. It facilitates diagnosing power problems, if any, in the extended alarm systems.

## Wireless devices

The window shows information about communication with the ABAX system wireless devices and keypads.

No. - number of zone or output to which the wireless device is assigned / address of the wireless keypad.

Name - name of zone or output to which the wireless device is assigned / name of the wireless keypad.

Device type - type of wireless device / keypad.

Serial number - serial number of wireless device / keypad.

Temperature - temperature indicated by the ATD-100 detector.

Signal level - level of radio signal received from the wireless device / keypad. Presented as a percentage.

Connection quality - quality of the communication with wireless device / keypad (expressed as a percentage ratio between the transmissions received and the transmissions expected).

Communication log - graphically presented information about quality of communication during the last 11 days.

###### Communication diagnostics

Test restart - click to reset information about connection quality and restart analyzing of communication data again.

Testing since - the date from which information about communication with wireless devices / keypads are analyzed.

###### Buttons

- click to open the Wireless system window.

Read communication log - click to refresh information presented in the Communication log column.

Close - click to close the window.

### Wireless system

The window presents in graphic form information about communication with the ABAX system wireless devices / keypads.

The level of radio signal of each wireless device / keypad of the ABAX system is presented in a separate tab. As long as the Wireless system window is open, the program is gathering the radio communication data, which may be written to disk. The data files may be opened later in the same window. The program writes the data to file automatically every 24 hours (the file name contains system name, date and time when written to disk).

Note: Closing the Wireless system window will terminate recording the data about signal level of individual devices / keypads.

Communication of the wireless device / keypad may be shown by using two diagram types: bar diagram (detailed) and linear diagram (long-term). The diagram shows levels from 0 do 100% and time scale.

An example of bar diagram. 1 - level of signal from wireless device. 2 - interference - maximum level. 3 - interference - medium level.

An example of linear diagram. 1 - level of signal from wireless device. 2 - interference - maximum level. 3 - interference - medium level.

# Configuration

Port RS-232

Modem

Data

## Port RS-232

Port RS-232 - select the computer COM port through which communication with the control panel RS-232 or USB port is to take place.

Notes:

Opening the Configuration window will result in closing the COM port that was previously selected for communication. After the window is closed, the COM port will be opened.

Where the USB-RS converter is being used, connect the converter prior to selecting the port. Do not disconnect the converter when the program is in use (disconnecting the converter during transmission of data may result in a computer hang).

## Modem

Use the tab to define parameters related to modem communication with the control panel.

After clicking on the  button you can configure parameters of the modem connected to computer (see: Configuring the modem connected to computer).

Dialing - the method of dialing numbers by the modem connected to computer (tone or pulse).

Dial tones control - if option is enabled, the modem connected to computer will detect the dial tone or busy signal before dialing the number.

Speaker - operating mode of the modem speaker. The speaker can be always OFF, or ON until connection with the control panel is established (auto), or always ON.

Volume - volume of modem speaker.

Answering - how the DLOADX program reacts when the control panel is connecting to the program. Communication can be established automatically after a preset number of rings, or the program will only indicate an attempt to establish communication by the control panel (communication will only be established after clicking on the Answer button).

Double call - you can define duration of the pause between the first and the second call, if the control panel is set to go off-hook after the second call.

### Configuring the modem connected to computer

Note: You can edit the parameters after clicking on the Change button.

Port RS-232 - computer COM port to which the modem is connected.

Modem - list of modems, the parameters of which are defined. The list of modems and their settings will be written to disk in the “modem.ini” file.

Baud Rate - transmission rate of the serial port. It is recommended that the highest rate acceptable by the modem be set (only some modems may require the 300 bps setting in order to enforce operation with exactly this speed).

Reset command - the command to reset the modem. Typically, it is the ATZ command (reset with restoration of the user's zero profile). Some modems may require using the AT&F command (reset with restoration of the factory default settings).

Initializing - lines containing the modem initialization commands:

for communication with built-in control panel 300 bps modem: in the first line E0V1Q0 - a command required for proper operation of the modem. You should also add the operating mode selection: B0 or B1 (selection of transmission format: V.21 or Bell103), and the commands limiting transmission rate over telephone line to 300 bps. These are commands specific for the given modem model, e.g. N0S37=3, F1 or +MS=1,0,300,300 etc. Information on how to limit the modem transmission rate is usually included in the device manual. The other line should contain the following commands: S0=0S9=1S7=120S10=255. They are necessary for correct operation.

for communication with external analog modem connected to the control panel: in the first line E0V1Q0, the second line S0=0S7=120. It is not recommended to insert additional commands to limit the modem transmission rate, unless this is required by the modems used, or the telephone link quality.

for communication through ISDN or GSM modem: in the first line E0V1Q0, the second line S0=0. Depending on the modems used, you will have to use additional commands to set the identical transmission format, as in the control panel modem, i.e. specific for the given modem. V.110 format is intended for the GSM modems.

Modem ISDN - enable this option, if communication is to be effected through an ISDN or GSM modem.

###### Buttons

Change - click to edit parameters of the selected modem or add a new modem to the list.

Test - click to test settings. The initialization window will show the initializing commands and the modem answers. The commands sent to the modem will always begin with the AT prefix. The modem acknowledges receiving the command with either OK or ERROR message (if the command is wrong). The MODEM NOT RESPONDING message means a wrongly selected COM port number or too high transmission rate.

OK - click to confirm the changes made and close the window.

Cancel - click to cancel the changes and close the window.

## Data

In this tab, you can specify location of the data catalog on the computer hard disk. The catalog is automatically created when the program is run for the first time.

Note: Changing location of the catalog which already contains some data written to it is not recommended, since it may cause loss of access to those data.

# Connection

Port COM

Modem 300bps

Modem - INTEGRA with ext. modem

Modem ISDN/GSM

TCP/IP: DLOADX -> ETHM

TCP/IP: DLOADX <- GSM/GPRS

TCP/IP: DLOADX <- ETHM/INT-GSM

TCP/IP: SATEL server

## Port COM

If the RS-232 or USB port of the control panel is connected with the computer, communication between the DLOADX program and the control panel can be established via the COM port. This enables the control panel to be programmed locally.

Computer connection to control panel RS-232 port. Shown on the left is RJ plug to be connected into the control panel mainboard socket. Shown on the right is DB-9 female plug (solder side view).

When the control panel is connected to the computer using the USB cable, the Windows system will automatically detect the connection of a new device and display a wizard that will guide you through the process of installation of the drivers for the new hardware. The drivers can be downloaded from www.satel.eu. Some versions of the Windows operating system may warn that the driver has not passed compatibility test. You should however continue installation of the drivers despite these warnings.

Notes:

Connecting the USB port to the computer will block the RS-232 port.

If the control panel is connected to other computer port than COM1, click on  in the main menu. The Configuration window will open, in which you can select the COM port to which the control panel is connected (Port RS-232).

The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Starting the local programming

- On the LCD keypad connected to the control panel, enter the service code (by default 12345) and press the * key.

- Using the arrow keys, find the Downloading submenu and press the # key.

- When the arrow indicates the Start DWNL-RS function, press the # key.

Note: To start the Start DWNL-RS function you can also use the shortcut: [service code]*01.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Emergency procedure of starting the local programming (“from pins”)

If the control panel does not support LCD keypads, does not accept the service code, etc., you can use the emergency procedure of, so-called, starting “from pins”. The computer must be connected to the control panel RS-232 port (the USB port cannot be used for the emergency procedure). Before proceeding to the steps described below, run the DLOADX program.

Note: Starting the local programming “from pins” is not possible, if the Disable Downloading option is enabled (see: Service).

- Turn off the control panel power supply (first disconnect the AC power, and then the battery).

- Put a jumper on the RESET pins located on the control panel mainboard.

- Turn on the control panel power supply (first connect the battery and then the AC power). The DIALER LED will start blinking.

- Wait a few seconds until the DIALER LED goes out and remove the jumper from the RESET pins. The Start DWNL-RS function will be started in control panel.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Finishing local programming

Note: The local programming function must be disabled, if the control panel is to communicate through the RS-232 port with an external analog modem, GSM module, INT-GSM module or ETHM-1 / ETHM-1 Plus module (e.g. during remote programming, event reporting, etc.).

You can finish the local programming function from the keypad:

- Enter the service code (by default 12345) and press the * key.

- Using the arrow keys, find the Downloading submenu and press the # key.

- When the arrow indicates the End DWNL-RS function, press the # key.

The local programming function will be finished automatically after 255 minutes have elapsed since the last use of the DLOADX program, and the service access was blocked or expired during that time.

## Modem 300bps

The control panel has a built-in 300 bps modem. If communication between the DLOADX program and the control panel is to take place via this modem, connect analog modem to the computer.

Note: The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Initiating a modem connection from DLOADX program

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

do not program the telephone number of modem connected to computer!

enable the Answering - modem option (Telephone),

define the number of rings after which the control panel will answer incoming calls - Rings before answer (Telephone),

enable the Double call option if the control panel is to answer only after the second call (Telephone).

Required settings of the DLOADX program:

program the telephone number of control panel (Connection settings window - you can open it by pressing Ctrl+R),

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem 300bps. Window with modem initialization information will be displayed.

- After modem initialization, click on the Connect button. Information on connection establishment will be displayed.

- When the control panel goes off-hook, the DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a modem connection from the DLOADX program, but the control panel calls back and makes the connection

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings),

enable the Answering - modem option (Telephone),

define the number of rings after which the control panel will answer incoming calls - Rings before answer (Telephone),

enable the Double call option if the control panel is to answer only after the second call (Telephone).

Required settings of the DLOADX program:

program the telephone number of control panel (Connection settings window - you can open it by pressing Ctrl+R),

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem 300bps. Window with modem initialization information will be displayed.

- After modem initialization, click on the Connect button. Information on connection establishment will be displayed.

- The control panel will receive the call, but will hang up. The DLOADX program will inform you that the control panel will call back.

- The control panel will call back the number of computer modem. The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection from the keypad (by control panel)

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings).

Required settings of the DLOADX program:

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem 300bps. Window with modem initialization information will be displayed.

- Ask the user to start the Start DWNL-TEL function (he is supposed to enter the code and press the * key, and then press in turn 0 and 4 keys). The control panel will call the computer modem number.

- The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## Modem - INTEGRA with ext. modem

You can connect an external analog modem to the control panel (see: Connecting the external modem to the control panel). If communication between the DLOADX program and the control panel is to take place via this modem, connect analog or GSM modem to the computer.

Note: The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Initiating a modem connection from DLOADX program

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

do not program the telephone number of modem connected to computer!

enable the External modem and Answering - modem options (Telephone),

define the number of rings after which the control panel will answer incoming calls - Rings before answer (Telephone),

enable the Double call option if the control panel is to answer only after the second call (Telephone).

Required settings of the DLOADX program:

program the telephone number of control panel (Connection settings window - you can open it by pressing Ctrl+R),

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem - INTEGRA with ext. modem. Window with modem initialization information will be displayed.

- After modem initialization, click on the Connect button. Information on connection establishment will be displayed.

- When the control panel goes off-hook, the DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a modem connection from the DLOADX program, but the control panel calls back and makes the connection

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings),

enable the External modem and Answering - modem options (Telephone),

define the number of rings after which the control panel will answer incoming calls - Rings before answer (Telephone),

enable the Double call option if the control panel is to answer only after the second call (Telephone).

Required settings of the DLOADX program:

program the telephone number of control panel (Connection settings window - you can open it by pressing Ctrl+R),

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem - INTEGRA with ext. modem. Window with modem initialization information will be displayed.

- After modem initialization, click on the Connect button. Information on connection establishment will be displayed.

- The control panel will receive the call, but will hang up. The DLOADX program will inform you that the control panel will call back.

- The control panel will call back the number of computer modem. The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection from the keypad (by control panel)

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings),

enable the External modem option (Telephone),

Required settings of the DLOADX program:

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem - INTEGRA with ext. modem. Window with modem initialization information will be displayed.

- Ask the user to start the Start DWNL-MOD function (he is supposed to enter the code and press the * key, and then press in turn 0 and 3 keys). The control panel will call the computer modem number.

- The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## Modem ISDN/GSM

You can connect an external GSM or ISDN modem to the control panel (see: Connecting the external modem to the control panel). If communication between the DLOADX program and the control panel is to take place via this modem, GSM or ISDN modem is to be connected to the computer (analog modem only if GSM modem is connected to the control panel).

Note: The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Initiating a modem connection from DLOADX program

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

do not program the telephone number of modem connected to computer!

enable the External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options (Telephone).

Required settings of the DLOADX program:

program the telephone number of control panel (Connection settings window - you can open it by pressing Ctrl+R),

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem ISDN/GSM. Window with modem initialization information will be displayed.

- After modem initialization, click on the Connect button. Information on connection establishment will be displayed.

- When the control panel goes off-hook, the DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a modem connection from the DLOADX program, but the control panel calls back and makes the connection

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings),

enable the External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options (Telephone).

Required settings of the DLOADX program:

program the telephone number of control panel (Connection settings window - you can open it by pressing Ctrl+R),

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem ISDN/GSM. Window with modem initialization information will be displayed.

- After modem initialization, click on the Connect button. Information on connection establishment will be displayed.

- The control panel will receive the call, but will hang up. The DLOADX program will inform you that the control panel will call back.

- The control panel will call back the number of computer modem. The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection from the keypad (by control panel)

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings),

enable the External modem and Modem ISDN/GSM/ETHM options (Telephone).

Required settings of the DLOADX program:

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem ISDN/GSM. Window with modem initialization information will be displayed.

- Ask the user to start the Start DWNL-MOD function (he is supposed to enter the code and press the * key, and then press in turn 0 and 3 keys). The control panel will call the computer modem number.

- The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a modem connection by using SMS message

This method of establishing connection is available, if the SATEL GSM module is connected to the control panel as external modem.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

program the telephone number of modem connected do computer (Connection settings),

enable the External modem and Modem ISDN/GSM/ETHM options (Telephone).

Required settings of the GSM module (you can configure them using the DLOAD10 program - see GSM module manual):

program the control command that will be sent in the SMS message to initiate modem connection between control panel and DLOADX program.

Required settings of the DLOADX program:

configure the modem communication parameters (Modem tab in the Configuration window).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click Modem ISDN/GSM. Window with modem initialization information will be displayed.

- Send to the phone number of GSM module the following SMS message:

xxxxxx. or xxxxxx= (“xxxxxx” - the control command programmed in the GSM module, initializing communication with the DLOADX program through modem) - the control panel will call, via the GSM module, the programmed computer telephone number,

xxxxxx=yyyy. or xxxxxx=yyyy= (“xxxxxx” - the control command programmed in the GSM module, initializing communication with the DLOADX program through modem; “yyyy” - computer telephone number to which the control panel is to connect) - the control panel will call, via the module, the telephone number sent in the SMS message (the computer telephone number programmed in the control panel will be ignored).

- The DLOADX program will receive the call automatically or you will have to accept establishing communication (see: Modem). The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## TCP/IP: DLOADX -> ETHM

Select TCP/IP: DLOADX -> ETHM if the DLOADX program is to connect to the control panel via ETHM-1 Plus / ETHM-1 module. The RS-232 ports of the module and the control panel must be connected (Connecting the RS-232 ports of control panel and ETHM-1 Plus / ETHM-1 / INT-GSM module).

Note: The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Initiating a connection from the DLOADX program

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the ETHM-1 Plus / ETHM-1 module (ETHM-1 / ETHM+GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

Communication with DLOADX option enabled,

programmed: the number of TCP port which will be used for communication and the data encryption key (DLOADX key),

network settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: Ethernet module address (Server), number of TCP port used for communication and data encryption key (DLOADX key).

Note: Before initiating the connection, make sure that the suitable connection establishing method is selected in the Connection settings window, Connection field.

- Click on the  button in main menu. A drop down menu will be displayed.

- Click in turn on TCP/IP: DLOADX -> ETHM and LAN/WAN (settings that you have entered yourself will be used) or LAN (provided the module is working in the same local network, settings of the module that was recently selected in the Connection field, Connection settings window, will be used). The Connection TCP/IP: DLOADX -> ETHM-1 window will be displayed.

- Click on the Connect button. Connection establishment information will be displayed.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## TCP/IP: DLOADX <- GSM/GPRS

Select TCP/IP: DLOADX <- GSM/GPRS if GPRS connection is to be established with the control panel to which an external SATEL GSM module is connected (Connecting the external modem to the control panel). The GSM-X module or a module with LEON telephone is required:

- GSM LT-1 with firmware version 1.14 (or newer),

- GSM LT-2 with firmware version 2.14 (or newer),

- GSM-4 with firmware version 4.14 (or newer),

- GSM-5 with firmware version 5.14 (or newer).

Notes:

The computer with DLOADX program must have a public IP address.

The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Initiating a connection by using SMS message

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the GSM module (you can configure them using the DLOAD10 program - see GSM module manual):

configured the GPRS settings (APN, user name, password, DNS server),

programmed: the network address of the computer with DLOADX program, the number of the TCP port that will be used for communication and the data encryption key,

programmed the control command which, if sent in the SMS message, will initiate connection with the DLOADX program,

additionally, you can enable the option that will enable connection to be established with the computer whose network address will be given in the SMS message initiating the connection.

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: DLOADX <- GSM/GPRS. The GSM->DLOADX, TCP/IP server window will be displayed.

- Enter the number of the TCP port that will be used for communication (Server port) and the data encryption key (DLOADX key).

- Click on the Start button. Activation of the server for GPRS connection will follow.

- Send to the phone number of GSM module the following SMS message:

zzzzzz. or zzzzzz= (“zzzzzz” - the control command programmed in the GSM module initializing GPRS communication with the DLOADX program) - the GSM module will connect the control panel to the computer whose address is programmed in the module,

zzzzzz=aaaa:p. or zzzzzz=aaaa:p= (“zzzzzz” - the control command programmed in the GSM module initializing GPRS communication with the DLOADX program; “aaaa” - address of the computer with DLOADX program (IP address or domain name); “p” - TCP port) - the GSM module will connect the control panel to the computer whose address is given in the SMS message (the computer address programmed in the GSM module will be ignored).

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## TCP/IP: DLOADX <- ETHM/INT-GSM

Select TCP/IP: DLOADX <- ETHM/INT-GSM if the control panel is to connect to the DLOADX program via ETHM-1 Plus / ETHM-1 / INT-GSM module. The RS-232 ports of the module and the control panel must be connected (Connecting the RS-232 ports of control panel and ETHM-1 Plus / ETHM-1 / INT-GSM module).

Notes:

The computer with DLOADX program must have a public IP address.

The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

###### Initiating a connection via the ETHM-1 Plus / ETHM-1 module from the keypad

Note: If the INT-GSM module is connected to the ETHM-1 Plus module and connection over Ethernet cannot be established, an attempt will be made to establish connection via GPRS.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the module (ETHM-1 / ETHM+GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

Communication with DLOADX option enabled,

programmed: the address of the computer with DLOADX program (DLOADX server), number of TCP port which will be used for communication and the data encryption key (DLOADX key),

network settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: the number of TCP port which will be used for communication and the data encryption key (DLOADX key) (or select the “LAN: ETHM-1, Address n” parameter set - the data programmed in settings of Ethernet module with “n” address will be used).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: DLOADX <- ETHM/INT-GSM. The Connection TCP/IP: DLOADX <- ETHM-1 window will be displayed.

- Ask the user to start the ETHM-1 ->DLOADX function (he is supposed to enter the code and press the * key, and then press in turn 0 and 7 keys). The control panel will connect to the computer network address.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection via the ETHM-1 Plus module using SMS message

Note: The INT-GSM module must be connected to the ETHM-1 Plus module. If connection via Ethernet cannot be established, an attempt will be made to establish communication via GPRS.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the module (ETHM+GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

Communication with DLOADX option enabled,

programmed: the address of the computer with DLOADX program (DLOADX server), number of TCP port which will be used for communication and the data encryption key (DLOADX key),

programmed control command, which, if sent in the SMS message, will initiate connection with the DLOADX program,

network settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: number of TCP port used for communication and data encryption key (DLOADX key).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: DLOADX <- ETHM/INT-GSM. The Connection TCP/IP: DLOADX <- ETHM-1 window will be displayed.

- Send to the INT-GSM module the following SMS message:

xxxx= (“xxxx” - the control command to initiate establishment of communication with DLOADX program) - the ETHM-1 Plus module will connect the control panel to the computer whose address is programmed in the module,

xxxx=aaaa:p= (“xxxx” - the control command to initiate establishment of communication with DLOADX program; “aaaa” - address of the computer with DLOADX program (IP address or domain name); “p” - TCP port) - the ETHM-1 Plus module will connect the control panel to the computer whose address is given in the SMS message and will use for communication the TCP port given in the SMS message.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection via the INT-GSM module from the keypad

Note: The method of establishing communication, as described below, applies to the INT-GSM module connected directly to the alarm control panel. If the INT-GSM module is connected to the ETHM-1 Plus module, see description of initiating a connection via the ETHM-1 Plus module.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the INT-GSM module (INT-GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

Communication with DLOADX option enabled,

programmed: the address of the computer with DLOADX program (DLOADX server), number of TCP port which will be used for communication and the data encryption key (DLOADX key),

GPRS settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: number of TCP port used for communication and data encryption key (DLOADX key).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: DLOADX <- ETHM/INT-GSM. The Connection TCP/IP: DLOADX <- ETHM-1 window will be displayed.

- Ask the user to start the INT-GSM ->DLOADX function (he is supposed to enter the code and press the * key, and then press in turn 0 and 9 keys). The control panel will connect to the computer network address.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection via the INT-GSM module by using SMS message

Note: The method of establishing communication, as described below, applies to the INT-GSM module connected directly to the alarm control panel. If the INT-GSM module is connected to the ETHM-1 Plus module, see description of initiating a connection via the ETHM-1 Plus module.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the INT-GSM module (INT-GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

Communication with DLOADX option enabled,

programmed: the address of the computer with DLOADX program (DLOADX server), number of TCP port which will be used for communication and the data encryption key (DLOADX key),

programmed control command, which, if sent in the SMS message, will initiate connection with the DLOADX program,

GPRS settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: number of TCP port used for communication and data encryption key (DLOADX key).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: DLOADX <- ETHM/INT-GSM. The Connection TCP/IP: DLOADX <- ETHM-1 window will be displayed.

- Send to the INT-GSM module the following SMS message:

xxxx= (“xxxx” - the control command to initiate establishment of communication with DLOADX program) - the INT-GSM module will connect the control panel to the computer whose address is programmed in the module,

xxxx=aaaa:p= (“xxxx” - the control command to initiate establishment of communication with DLOADX program; “aaaa” - address of the computer with DLOADX program (IP address or domain name); “p” - TCP port) - the INT-GSM module will connect the control panel to the computer whose address is given in the SMS message and will use for communication the TCP port given in the SMS message.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## TCP/IP: SATEL server

Select TCP/IP: SATEL server if communication between the DLOADX program and the control panel is to be established via the SATEL server. The ETHM-1 Plus or INT-GSM module must be connected to the control panel. The RS-232 ports of the module and the control panel must be connected (Connecting the RS-232 ports of control panel and ETHM-1 Plus / ETHM-1 / INT-GSM module).

Notes:

The communication identifiers in control panel and program must be identical, or the control panel identifiers must have their factory default value (see: Communication identifiers and establishing connection).

For communication via the SATEL server, the ports of 1024-65535 range are used as outgoing ports. These ports must not be blocked.

###### Initiating a connection in the case of communication via the ETHM-1 Plus module

Note: If the INT-GSM module is connected to the ETHM-1 Plus module and connection over Ethernet cannot be established, an attempt will be made to establish connection via GPRS.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the module (ETHM-1 / ETHM+GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

- Communication with DLOADX and Connection via Satel server options enabled,

data encryption key (DLOADX key) programmed,

network settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: identification number assigned to the ETHM-1 Plus module by the SATEL server (ETHM-1 ID), MAC address of the ETHM-1 Plus module (ETHM-1 MAC) and data encryption key (DLOADX key).

Note: For communication via the SATEL server, the ports of 1024-65535 range are used as outgoing ports. These ports must not be blocked.

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: Satel server. The Connection TCP/IP: DLOADX <-> ETHM-1 window will be displayed.

- Click on the Connect button. Connection establishment information will be displayed.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

###### Initiating a connection in the case of communication via the INT-GSM module

Note: The method of establishing communication, as described below, applies to the INT-GSM module connected directly to the alarm control panel. If the INT-GSM module is connected to the ETHM-1 Plus module, see description of initiating a connection via the ETHM-1 Plus module.

Required settings of the control panel (you can configure them using the keypad or during programming via the COM port (Port COM)):

External modem, Modem ISDN/GSM/ETHM and Answering - ETHM/GSM options enabled (Telephone).

Required settings of the INT-GSM module (INT-GSM) (you can configure them using the keypad or during programming via the COM port (Port COM)):

- Communication with DLOADX and Connection via Satel server options enabled,

data encryption key (DLOADX key) programmed,

GPRS settings configured.

Required settings of the DLOADX program (Connection settings window - you can open it by pressing Ctrl+R):

programmed: identification number assigned to the INT-GSM module by the SATEL server (INT-GSM ID), IMEI number of the INT-GSM module (INT-GSM IMEI) and data encryption key (DLOADX key).

- Click on the  button in main menu. A drop down menu will be displayed.

- Click TCP/IP: Satel server. The Connection TCP/IP: DLOADX <-> ETHM-1 window will be displayed.

- Click on the Connect button. Connection establishment information will be displayed.

- The DLOADX program will inform you about establishing the connection by displaying an appropriate message. The message contents depends on whether the program has been connected to a new alarm system, or a system whose data have already been saved (see: Communication identifiers and establishing connection).

## Connecting the external modem to the control panel

The control panel can work with any external modem having a RS-232 port compatible with the Hayes AT standard. The external modem or the communication module (GSM or ISDN) used as an external modem must be connected to the control panel RS-232 port (see figures).

Note: If the SATEL GSM module is to work in conjunction with the INTEGRA Plus control panel as the external modem, do not enable the Fax/Modem option in it.

Connecting the external analog modem to the control panel.

Connecting the MDM56 BO modem to the control panel.

Connection of the RS-232 ports of control panel and modem with the DB-9 socket. Shown on the left is RJ plug to be connected into the control panel mainboard socket. Shown on the right is DB-9 male plug (solder side view).

The way of connecting to the control panel RS-232 port the following devices:

- MDM56 BO external modem,

- SATEL GSM module which is to work as external modem,

- ETHM-1 Plus / ETHM-1 Ethernet module,

- INT-GSM module.

Shown on the left is RJ plug to be connected into the control panel mainboard socket. Shown on the right is PIN-5 plug. A ready cable is offered by SATEL company (RJ/PIN5).

Configuring the modem to be connected to control panel

### Configuring the modem to be connected to control panel

Note: The MDM56 and MDM56 BO modems, manufactured by SATEL, do not require any configuration. The factory settings ensure correct work with the control panel.

Before connecting to the control panel, connect the modem to the computer and, using the Terminal type program, set the correct operating mode.

- Enter the at command - the modem should respond with “OK”. Otherwise, enter ate1. If the modem fails to respond, check the modem connection to the computer, and make sure that the correct COM port is selected in the Terminal program settings.

- Enter the at&v command. The modem will present a list of parameters to be programmed. The parameter block saved as the “profile 0” should include E1 Q0 V1 X4 &D2 &S0 and S00:000. In such a case the modem is ready for operation with the control panel.

- If any parameter is set differently, it should be modified. The parameter setting command consists of a fixed AT prefix and the desired parameter setting (e.g., if E0 V0 is included in the profile, the command for setting the proper value will be ate1v1, after which the modem will answer “OK”).

- Enter the at&w0 command to save the settings in the “profile 0”.

- Enter the atz command followed by at&v to check that all parameters are saved correctly. The settings in ACTIVE PROFILE should be the same as in STORED PROFILE 0 (Note: Often the STORED PROFILE contains less parameters than the ACTIVE PROFILE, which is normal).

Notes:

To set the S0 modem register, use the ats0=0 command.

When restarting the modem, the control panel gives the ATZ command, which sets the parameters as stored in the “profile 0”. For this reason, the current setting of the parameters mentioned in it. 2 (“ACTIVE PROFILE”) is irrelevant, but it is important that they be set properly in the “profile 0”.

## Connecting the RS-232 ports of control panel and ETHM-1 Plus / ETHM-1 / INT-GSM module

The figure below shows how to connect the RS-232 ports of control panel and ETHM-1 Plus / ETHM-1 / INT-GSM module. A ready cable is offered by SATEL company (RJ/PIN5).

## Communication identifiers and establishing connection

###### Establishing communication with a new alarm system

If the factory default identifiers are programmed in the control panel, the program will inform that communication has been established with a new alarm system. A window will be displayed in which you will be able to give a name to the new system, and in which the program will suggest randomly generated identifiers instead of the factory default ones. The identifiers can be freely changed. After closing the window, the program will read all data from the control panel and write the new communication identifiers to the control panel. If the system data are written to the computer hard disk, the program will identify the control panel and choose a data file to match it.

###### Establishing communication with a system whose data are in the computer

If, based on the communication identifiers, the program determines that the alarm system data are written to the computer, it will suggest opening the file that contains those data.

###### Establishing communication with a system whose data are not in the computer

If, based on the communication identifiers, the program determines that the alarm system data are not written to the computer, while they are not also the factory default identifiers, establishing communication will only be possible after identifiers consistent with those programmed in the control panel are programmed in the Connection settings window (available in the drop-down menu after you click on the Communication command in the main menu). You can check the identifiers in the control panel by means of the LCD keypad (Service mode >SM settings).

# Communication

Communication options

Connection settings

## Communication options

The window enables configuration of the rules for data reading from and writing to the control panel.

Mode: "AUTO" - if the option is enabled, the program downloads from the control panel the data that have been changed since synchronization of the program and control panel data. Thus the time of data reading can be minimized. If there is a difference between the data in control panel and computer, the Data comparison: Write window will be displayed. If this option is disabled, all data are read.

Write only changes - if this option is enabled, writing data to the control panel will be limited to the data that have been changed. If the option is disabled, all data are written.

###### Buttons

- click to synchronize program data and control panel data (read/write data).

- click to write data to the control panel.

- click to terminate data reading/writing.

Close - click to close the window.

### Data comparison: Write

The window is displayed, if during reading/writing data differences were found between the program settings and the control panel settings. The data are compared only when reading in the AUTO mode.

Changed in PC - list of changes that have been made to settings in program since the last synchronization.

Read from Integra - list of changes that have been made to settings in control panel since the last synchronization.

###### Buttons

Undo change - click to cancel the highlighted change to settings in program. The button is available after you click on the list of changes made to the program.

Undo all changes - click to cancel all changes made to settings in program. The button is available after you click on the list of changes made to the program.

Load to PC - click to copy to the settings in program the highlighted change made to the settings in control panel. The button is available after you click on the list of changes made to the control panel.

Load all - click to copy to the settings in program all changes made to the settings in control panel. The button is available after you click on the list of changes made to the control panel.

Write as in PC - click to cancel all changes made to the control panel.

Next - click to write the changes in settings. First, the changed data from the control panel are written to the computer, and then the changes made to the computer are written to the control panel. This order of writing means that, in case of making changes to the same data in computer and control panel, the changes in the control panel will have priority.

Cancel - click to terminate data reading/writing.

## Connection settings

###### Panel INTEGRA

INTEGRA identifier - identifier of the alarm control panel. It must consist of 10 characters (digits or letters from A to F). It makes it possible to recognize the control panel and match a data file to it, if the data file has been saved on the computer. Do not program the same identifier for different control panels which are operated from the same computer (the DLOADX program will be incapable of distinguishing between them). Click  to see the sequence of characters.

Note: In case of establishing communication with the alarm system whose identifier have factory defaults, the DLOADX program will suggest random generated identifier.

Panel’s tel. no - telephone number of the control panel.

###### PC - DloadX

DLOADX identifier - identifier of the computer with DLOADX program. It must consist of 10 characters (digits or letters from A to F). The control panel will only establish connection with the program which uses the valid identifier. Click  to see the sequence of characters.

PC phone number - telephone number of the modem connected to computer with DLOADX program installed.

###### PC - GUARDX

GUARDX identifier - identifier of the computer with GUARDX program. It must consist of 10 characters (digits or letters from A to F). The control panel will only establish connection with the program which uses the valid identifier. Click  to see the sequence of characters.

PC phone number - telephone number of the modem connected to computer with GUARDX program installed.

###### ACCO NET

ACCO identifier - identifier for purposes of integration with ACCO NET system. It consist of 8 digits. Click  to see the sequence of characters.

###### TCP/IP connection: DLOADX - ETHM/INT-GSM

The settings below apply to direct communication with the ETHM-1 Plus / ETHM-1 / INT-GSM module.

Connection - the method of configuring the parameters required for establishing communication:

LAN/WAN - you can enter the parameters yourself.

LAN: ETHM-1, Address n [n=module address] - settings of the ETHM-1 Plus / ETHM-1 module with the given address will be used (the module network address will not be read if it is downloaded from the DHCP server). These settings can only be used for the needs of LAN communication.

GSM: INT-GSM, Address n [n=module address] - settings of the INT-GSM module with the given address will be used.

Server - address of the ETHM-1 Plus / ETHM-1 module. If the Ethernet module is not in the same local network as the computer with DLOADX program, it must be a public address. You can enter either the IP address or the domain name.

Port - the number of TCP port used for communication between the control panel and computer with DLOADX program via ETHM-1 Plus / ETHM-1 / INT-GSM module. You can enter a value from 1 to 65535. Default value: 7090.

DLOADX key - a string of up to 12 alphanumeric characters (digits, letters and special characters), used for data encryption during communication between the control panel and the computer with DLOADX program via ETHM-1 Plus / ETHM-1 / INT-GSM module. Click  to see the sequence of characters.

###### Satel server

The settings below apply to communication with the ETHM-1 Plus module (ETHM-1 ID, ETHM-1 MAC and DLOADX key) / INT-GSM module (INT-GSM ID, INT-GSM IMEI and DLOADX key) via the SATEL server.

Connection - the method of configuring the parameters required for establishing communication:

MAC (ETHM-1) - you can enter yourself the parameters for communication with the ETHM-1 Plus module.

IMEI (INT-GSM) - you can enter yourself the parameters for communication with the INT-GSM module.

Module: ETHM-1, Address n [n=module address] - settings of the ETHM-1 Plus module with the given address will be used.

Module: INT-GSM, Address n [n=module address] - settings of the INT-GSM module with the given address will be used.

ETHM-1 ID - individual identification number assigned to the ETHM-1 Plus module by the SATEL server. Click  to see the sequence of characters.

ETHM-1 MAC - hardware address of ETHM-1 Plus module. Click  to see the sequence of characters.

INT-GSM ID - individual identification number assigned to the INT-GSM module by the SATEL server. Click  to see the sequence of characters.

INT-GSM IMEI - individual identification number of the GSM telephone of INT-GSM module. Click  to see the sequence of characters.

DLOADX key - a string of up to 12 alphanumeric characters (digits, letters and special characters), used for data encryption during communication between the control panel and the computer with DLOADX program via ETHM-1 Plus / ETHM-1 / INT-GSM module. Click  to see the sequence of characters.

# Programming telephone numbers

When programming a telephone number, you can use all the characters defined in the DTMF standard, i.e. digits from 0 to 9 and special characters:

B - switch-over to pulse dialing;

C - switch-over to tone dialing (DTMF);

D - waiting for additional signal;

E - 3 second pause;

F - 10 second pause;

* - signal * in DTMF mode;

# - signal # in DTMF mode;

a, b, c, d - other signals generated in DTMF mode.

Note: Do not overuse the control characters. They are only to be used when necessary. There is no need for putting them at the beginning, before the telephone number digits. The basic method of dialing, appropriate pause and awaiting the dial tone before dialing are set in the telephone options (see: Telephone).