The SPP-100 / SPP-101 fire alarm sounder meets the essential requirements of the Regulation of the European Parliament and of the Council (EU) No. 305/2011 and the European Union Directives:

CPD 89/106/EEC Construction Products Directive;

EMC 2014/30/EU Electromagnetic Compatibility Directive;

An EC Certificate of Conformity No. 1438-CPR-0343 was issued by the CNBOP-PIB Jozefow Certification Body for the SPP-100 / SPP-101 fire alarm sounder to confirm its compliance with the requirements of PN-EN 54-3:2003 + PN-EN 54-3:2003/A2:2007 standards.

The Certificate of Conformity can be downloaded from the www.satel.eu website.

13

SATEL Sp. z o.o. • ul. Budowlanych 66 • 80-298 Gdańsk • POLAND 1438 1438-CPR-0343

DOP/CPR/0343 EN 54-3 Fire safety. Fire alarm sounder SPP-100 (type A), SPP-101 (type B) Declaration of Performance No. DOP/CPR/0343

This manual covers the following products:

SPP-100	-	fire alarm sounder with a low base (Fig. 1);

SPP-101	-	fire alarm sounder with a high base (Fig. 2).

The fire alarm sounders provide information about fire by means of acoustic signals. They are designed to be used in conjunction with the CSP-104, CSP-108, CSP-204 and CSP-208 fire alarm control panels.

Prior to installation, please read this manual carefully in order to avoid any mistakes and/or errors which might result in malfunctioning of or even damage to the equipment. The manual contains guidelines for installation of the fire alarm sounders and their connection to the fire alarm control panel.

# Features

Acoustic signaling by means of piezoelectric transducer.

32 selectable tones.

Selectable volume level.

# Functional description

After voltage is applied to the appropriate terminals, acoustic signaling will be activated. The tone depends on the settings of DIP-switches.

# Installation

Disconnect power before making any electrical connections.

- Run the cables into the enclosure base. For the SPP-100 sounders, you can make additional holes in the enclosure (Fig. 3). In the case of SPP-101 sounders, you must make holes for the cable glands (Fig. 4).

- Secure the enclosure base to the wall.

- Set the volume and select the tone (see section Selecting the tone and setting the volume).

- Screw the wires to the corresponding terminals. Fig. 5 shows a typical connection of the fire alarm sounders to the fire alarm control panel.

- Replace the enclosure cover and secure it with the lock screw.

## Selecting the tone and setting the volume

To select the tone to be triggered after voltage is applied, use the DIP-switches, designated by digits from 1 to 5 (see Fig. 6). The tones and the way of setting the DIP-switches are described in the table below (DIP-switch in position ON = 1).

The DIP-switch designated VOL is used to set the signal volume level. When the switch is in the ON position, the maximum volume of signaling is set (the recommended setting).

For detailed information about the sound intensity (volume) in accordance with EN54-3, please refer to SPP-100-spl.

# Maintenance

The fire alarm sounders should be subject to regular checks to ensure they are working correctly. Periodic checks should be conducted at least every six months.

# Specifications

Supply voltage	18...28 V DC

Standby current consumption	0 mA

Maximum current consumption	32 mA

Operating temperature range	-25...+70 °C

Maximum humidity	933%

Protection rating	SPP -100	IP54

SPP -101	IP65

Enclosure dimensions	SPP-100	93 x 93 x 63 mm

SPP-101	93 x 93 x 91 mm

Weight	SPP-100	174 g

SPP-101	206 g

FIRE ALARM SOUNDER

SPP-100

SPP-101

Installation Manual

spp-100_en 07/19

SATEL sp. z o.o.

ul. Budowlanych 66

80-298 Gdańsk

POLAND

tel. + 48 58 320 94 00

www.satel.eu

druk (2 na 1)

6,7,0,5,4,1,2,3