INT-CR

PROXIMITY CARD ARM/DISARM DEVICE

int-cr_sii_en 01/20

Quick installation guide

Full manual is available on www.satel.eu

The INT-CR device is designed for arming / disarming partitions as well as clearing alarms using proximity cards. The device is compatible with the INTEGRA (firmware version 1.07 or newer) / INTEGRA Plus / VERSA / VERSA Plus / VERSA IP control panels.

# Installation

Disconnect power before making any electrical connections.

The device is designed for indoor installation.

If the device is installed on a metal surface, the card reading range will be reduced.

The distance to another device with proximity card reader should be at least 50 centimeters.

If you need an extra cable to make the connections, use an unshielded non-twisted cable. If you use the twisted-pair type of cable, remember that CLK (clock) and DTA (data) signals must not be sent through one twisted pair. The distance between the device and the control panel can be up to 1000 meters (INTEGRA / INTEGRA Plus) / 600 meters (VERSA / VERSA Plus / VERSA IP).

- Remove the device cover (Fig. 2).

- Place the enclosure base against the wall and mark the location of mounting holes.

- Drill holes for wall plugs (anchors) in the wall.

- Make a hole in the wall for the device cable and run the cable through it.

- Using wall plugs (anchors) and screws, secure the enclosure base to the wall. Select wall plugs specifically intended for the mounting surface (different for concrete or brick wall, different for plaster wall, etc.).

- Set the device address (see “Address setting”).

- Replace the cover and secure it with the screw.

- Connect the wires to the control panel screw terminals according to the table below. If the distance to the control panel exceeds 300 meters, use an additional power supply to power the device.

| Wire | Description | Terminals |
| --- | --- | --- |
|  |  | INTEGRA / INTEGRA Plus | VERSA / VERSA Plus / VERSA IP |
|  | brown | power | +EX / +EX1 / +EX2 | AUX / KPD |
|  | white | common ground | COM | COM |
|  | gray | clock | CK / CK1 / CK2 | CLK |
|  | green | data | DT / DT1 / DT2 | DTA |

- Power on the alarm system.

- Start the identification function in the control panel (see the control panel installer manual). The device will be identified as INT-IT.

## Address setting

An individual address (different from that in the other devices connected to the control panel bus) must be set in the device. Depending on the control panel:

INTEGRA / INTEGRA Plus: set an address in the range from 0 to 31,

VERSA / VERSA Plus / VERSA IP: set an address in the range from 16 to 21.

To set the address, use the DIP switches on the device electronics board. The switches have numbers assigned to them. The number for OFF position is 0. The numbers assigned to the switches in ON position are presented in the table below. The sum of these numbers is the address set.

| Switch (ON position) | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Number | 1 | 2 | 4 | 8 | 16 |

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o. • ul. Budowlanych 66 • 80-298 Gdańsk • POLAND

tel. +48 58 320 94 00

www.satel.eu

druk (4 na 1)

1,2,1,2,1,2,1,2