INT-S

Partition keypad

int-s_sii_en 07/20

# Quick installation guide

Full manual is available on www.satel.eu

The alarm system should be installed by qualified personnel.

Before installation, please read the full manual thoroughly.

Disconnect power before making any electrical connections.

The INT-S partition keypad offers control of one partition in the alarm system and provides access control features. The device can be used in conjunction with the INTEGRA and INTEGRA Plus control panels.

The keypad is designed for indoor installation. The place of installation should be readily accessible to the system users.

- Open the keypad enclosure.

- Set the partition keypad address (see “Setting address”).

- Place the enclosure base on the wall and mark the location of mounting holes.

- Drill the holes for wall plugs (anchors).

- Run the wires through the opening in the enclosure base.

- Using wall plugs (anchors) and screws, fasten the enclosure base to the wall. Select wall plugs specifically intended for the mounting surface (different for concrete or brick wall, different for drywall, etc.).

- Connect the CLK, DTA and COM terminals to the appropriate terminals of the control panel expander bus (see the control panel installer manual). It is recommended that an unshielded non-twisted cable be used for making the connection. If you use the twisted-pair type of cable, remember that CLK (clock) and DTA (data) signals must not be sent through one twisted-pair cable. The wires must be run in one cable.

- If the partition keypad is to control an electric strike, electromagnetic lock or another door actuator, connect this device to the NO terminals as shown in Fig. 1. It is not recommended that the door actuator be powered from the same source as the partition keypad.

- If the keypad is to supervise the door status, connect the detector supervising the door status to the IN and COM terminals. If the keypad is not to supervise the door status, connect the IN terminal to the COM terminal or, when configuring the keypad, set value 0 for the “Max. door open time” parameter.

- Connect the power wires to the 12V and COM terminals. The keypad may be powered directly from the control panel, from an expander with power supply or from a power supply unit.

- Close the keypad enclosure.

- Power on the alarm system.

- Start the identification function in the control panel (see the control panel installer manual). The keypad will be identified as “INT-S/SK”.

## Address setting

To set the address, use the DIP switches on the electronics board. The switches have numbers assigned to them. The number for OFF position is 0. The numbers assigned to the switches in ON position are presented in the table below. The sum of these numbers is the address set.

| Switch (ON position) | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Number | 1 | 2 | 4 | 8 | 16 |

Figures 2 and 3 show examples of addresses set by using DIP switches.

## Description of terminals

NO	-	relay output

12V	-	power input

DTA	-	data (expander communication bus)

CLK	-	clock (expander communication bus)

COM	-	common ground

IN	-	door status monitoring input (NC)

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o. • ul. Budowlanych 66 • 80-298 Gdańsk • POLAND

tel. +48 58 320 94 00

www.satel.eu

druk (4 na 1)

2,1,2,1,2,1,2,1