AQUA Plus 2E

DIGITAL PASSIVE INFRARED DETECTOR

aqua_plus_2E_en 04/12

The AQUA Plus 2E detector can detect motion in a protected area. It is dedicated to be used with control panels which support the 2EOL/NC (2 x 1.1 k() configuration.

# Features

Dual element pyrosensor.

Built-in EOL resistors.

Digital motion detection algorithm.

Pre-alarm feature.

Two-way pyrosensor signal analysis, based on value and quantity.

Digital temperature compensation.

Low supply voltage signaling (voltage drop below 9 V ±5%).

LED indicator.

Tamper protection against cover removal.

Adjustable mounting bracket included.

# Electronics board

alarm output terminals (to be connected to control panel zone programmed as 2EOL/NC).

terminals to connect +12 V DC power.

red color LED to indicate:

- prealarm – short flash (approx. 120 ms);

- alarm – ON for 2 seconds;

- warm-up – blinking rapidly;

- low supply voltage – ON.

pyroelectric sensor.

tamper contact (NC).

scale for positioning of pyroelectric sensor against the lens (see: Fig. 7).

fixing screw hole.

detector configuration pins:

PIR SENS.	-	setting the detector sensitivity. Shown in Fig. 2 are the available sensitivity settings: A – low, B and C – medium, D – high [ - pins shorted;  – pins open].

LED ON/OFF	-	enabling/disabling the LED indicator. The LED indicator is enabled when the pins are shorted.

# Coverage area

Figure 3 shows the coverage area for a detector with the EWA lens, which is mounted as standard but can be replaced with another one:

LR – long range array: range 30 m; main beam 3 m wide at the end of range.

VB – vertical barrier array: range 22.5 m; beam 2.2 m wide at the end of range.

# Installation

Do not touch the pyroelectric sensor, so as not to soil it.

- Remove the front cover (Fig. 4).

- Remove the electronics board.

- Make the openings for screws and cable in the enclosure base.

- Pass the cable through the prepared opening.

- Fix the enclosure base to the wall (Fig. 5) or to the bracket (Fig. 6).

- Fasten the electronics board, taking into consideration the height of detector installation (Fig. 7).

- Connect the wires to the corresponding terminals.

- Using jumpers, set the working parameters of the detector.

- Replace the cover.

# Start-up

- Power-up the detector. The LED will start blinking (if the LED ON/OFF pins are shorted).

- When the LED will stop blinking, carry out the detector range test, i.e. check that movement within the coverage area will activate the alarm relay and lighting of the LED.

- If necessary, change the detector sensitivity (pins PIR SENS.).

# Specifications

Supply voltage	12 V DC 15%

Standby current consumption	10 mA

Maximum current consumption	12 mA

EOL resistors	2 x 1,1 k(

Alarm signaling period	2 s

Warm-up period	30 s

Detectable speed	0.3...3 m/s

Standards complied with	EN50130-5, EN50131-1, EN50131-2-2, EN50130-4

Security grade according to EN50131-2-2	Grade 2

Environmental class according to EN50130-5	II

Operating temperature range	-30...+55 °C

Maximum humidity	933%

Recommended installation height	2.4 m

Dimensions	63 x 96 x 49 mm

Weight	88 g

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o.

ul. Schuberta 79

80-172 Gdańsk

POLAND

tel. + 48 58 320 94 00

info@satel.pl

www.satel.pl

druk (4na1):

4,1,4,1,2,3,2,3