CA-64 E

ca64e_int 01/11

ZONE EXPANDER

The CA-64 E zone expander can be used in conjunction with CA-64, INTEGRA and VERSA control panels. This manual applies to the expander with electronics version 2.3 and firmware version 2.01 (or newer).

# Features

8 programmable zones:

support for NO and NC type detectors, as well as roller shutter motion detectors and vibration detectors;

support for single EOL and double EOL loops.

Programmable end-of-line resistors value.

Additional tamper input, NC type.

# Electronics board

FIGURE 1. View of the expander electronics board.

1	-	STATUS LED:

- blinking – data exchange with the panel;

- illuminated – no communication with the control panel.

2	-	a set of DIP-switches (see: DIP-switches).

Description of the terminals:

Z1...Z8	-	zones.

COM	-	common ground.

TMP	-	tamper loop input (NC) – if no tamper contact is connected to this terminal, it should be shorted to common ground.

CLK	-	clock.

DTA	-	data.

+12V	-	expander power supply input / detectors power supply output.

# DIP-switches

Use the switches 1-5 to set an address. The address must be different from that of the other modules connected to the communication bus of alarm control panel. In case of interaction with the VERSA control panel, an address from the 12 (0Ch) to 14 (0Eh) range must be set. In order to determine the expander address, add up the values set on individual switches as shown in Table 1.

| DIP-switch number | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Numerical value (for switch in ON position) | 1 | 2 | 4 | 8 | 16 |

Table 1.

The switches 6 and 7 must be set to OFF position.

Use the switch 8 to define how the expander will be identified by the control panel:

OFF – CA-64 E. The expander does not support roller shutter motion detectors and vibration detectors. Programming the end-of-line resistors value is not available.

ON – CA-64 Ei. The expander supports roller shutter motion detectors and vibration detectors. Programming the end-of-line resistors value is available (make sure that a suitable value is programmed).

The switch 8 must be in position OFF for the CA-64 control panel and for the INTEGRA panels with firmware up to and including version 1.04. These control panels do not support the CA-64 Ei expander.

FIGURE 2. Examples of address setting (address 14 (0Eh) is one of the addresses required for interaction with the VERSA series control panels).

# Installation and start-up

Disconnect power before making any electrical connections.

The expander should be installed indoors, in spaces with normal humidity of air. The connections should be made with the typical unscreened straight-through cable (using the "twisted pair" type of cable is not recommended).

- Fasten the expander board in the enclosure.

- Using the DIP-switches, set the suitable expander address and define how it is to be identified.

- Wire the CLK, DTA and COM terminals to the corresponding terminals of the control panel communication bus (see: installer manual for alarm control panel). The wires must be run in one cable.

- Wire the enclosure tamper contact to the TMP and COM terminals (or short the TMP terminal to the COM terminal).

- Complete the zone wiring (for wiring description refer to the alarm control panel installer manual).

- Connect power supply wires to the +12V and COM terminals. Supply may be provided from the control panel mainboard, from an additional power supply unit or from an expander with power supply (see: installer manual for alarm control panel).

- Turn on power supply of the alarm system.

- Start the identification function in the control panel. When the identification is completed, the zones will be assigned respective numbers in the alarm system (zone numeration rules are described in the alarm control panel manual).

# Specifications

Number of programmable zones	8

Supply voltage	12 V DC 15%

Standby current consumption	70 mA

Maximum current consumption	70 mA

Complied with standards	EN 50130-4, EN 50130-5, EN 50131-1, EN 50131-3

Security grade according to EN50131	Grade 3

Environmental class according to EN50130-5	II

Operating temperature range	-10 °C…+55 °C

Maximum humidity	933%

Dimensions of electronics board	57 x 80 mm

Weight	47 g

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o.

ul. Schuberta 79

80-172 Gdańsk

POLAND

tel. + 48 58 320 94 00

info@satel.pl

www.satel.pl