COBALT

COBALT Plus

COBALT Pro

DIGITAL DUAL TECHNOLOGY MOTION DETECTOR

cobalt_en 07/15

The COBALT / COBALT Plus / COBALT Pro detector allows detection of motion in the protected area. This manual applies to the detector with electronics version Q (or newer).

# FEATURES

Passive infrared (PIR) sensor and microwave sensor.

Dual [COBALT, COBALT Plus] or quad [COBALT Pro] element pyrosensor.

Adjustable detection sensitivity of microwave sensor.

Selectable detection sensitivity of passive infrared sensor.

Digital motion detection algorithm.

Digital temperature compensation.

Selectable operation modes: basic or counting.

Microwave based anti-mask feature [COBALT Plus / COBALT Pro].

Built-in EOL resistors (Double EOL).

Bi-color LED to indicate motion detection / alarm status.

Supply voltage control.

Tamper protection against cover removal.

# DESCRIPTION

## Operation modes

Basic – the detector indicates an alarm if both sensors detect motion within a time period shorter than 10 seconds.

Counting – the detector indicates an alarm if:

both sensors detect motion within a time period shorter than 10 seconds,

within 30 minutes' period, the microwave sensor detects motion 16 times, but PIR sensor does not detect any motion.

## Anti-mask feature

Detection by the microwave sensor of an object moving at a distance of 10-20 centimeters from the detector is interpreted as an attempt to mask the detector and results in activation of anti-masking relay for two seconds. Objects permeable to microwaves, but isolating the infrared radiation are not detected by the anti-mask feature.

## Supply voltage control

In the event of the voltage drop below 9 V (± 5%) for more than 2 seconds, the detector will signal a trouble. The trouble is indicated by the activation of alarm relay and the steady red light of LED indicator. The trouble signaling will continue as long as the trouble persists.

# ELECTRONICS BOARD

terminals:

WRN	-	anti-masking output (NC relay) [only COBALT Plus and COBALT Pro].

TMP	-	tamper output (NC).

COM	-	common ground.

12V	-	power input.

NC	-	alarm output (NC relay).

configuration pins for detector outputs:

the built-in resistors are to be used – place the jumpers as shown in Fig. 2 (connect the outputs as shown in Fig. 10),

the built-in resistors are not to be used – place the jumpers as shown in Fig. 3 (connect the outputs as shown in Fig. 9).

microwave sensor.

bi-color LED to indicate:

- alarm – the LED lights red for 2 seconds,

- motion detected by one of the sensors – the LED lights green for 2 seconds,

- trouble – the LED lights red,

- warm-up – the LED is blinking alternately red and green.

PIR sensor. Do not touch the pyroelectric sensor, so as not to soil it.

tamper switch.

detector configuration pins:

PIR SENS. 	-	selecting the PIR sensor sensitivity – see: Fig. 4 (A – low sensitivity, B and C – medium sensitivity, D – high sensitivity).

MODE	-	selecting the detector operation mode (jumper installed – basic mode; jumper removed – counting mode).

LED	-	enable/disable the LED indicator (jumper installed – LED enabled; jumper removed – LED disabled).

potentiometer for adjustment of the microwave sensor sensitivity. Please bear in mind that microwaves can penetrate e.g. glass, gypsum walls, non-metallic doors, etc.

fixing screw hole.

# INSTALLATION

- Remove the front cover (Fig. 5).

- Remove the electronics board.

- Make the openings for screws and cable in the enclosure base.

- Pass the cable through the prepared opening.

- Secure the enclosure base directly to the wall or to the bracket screwed down to the wall/ceiling (Fig. 6 and 7).

- Fasten the electronics board.

- Connect the wires to the corresponding terminals.

- Using potentiometer and jumpers, set the detector working parameters.

- Replace the cover.

# START-UP AND WALK TEST

Note:	When testing the detector, the LED should be enabled.

- Power-up the detector. The LED will begin alternately blinking red and green, which indicates the detector warm-up.

- When the LED stops blinking, check that moving within the coverage area will activate the alarm relay and make the LED light up red. Fig. 8 shows the maximum coverage area (maximum sensitivity).

# SPECIFICATIONS

Supply voltage	12 V DC 15%

Standby current consumption	14 mA

Maximum current consumption	20 mA

EOL resistors	2 x 1.1 k(

Relay contacts rating (resistive load)	40 mA / 16 V DC

Microwave frequency	10.525 GHz

Detectable speed	0.3...3 m/s

Alarm signaling period	2 s

Warm-up period	30 s

Recommended installation height	2.4 m

Security grade according to EN50131-2-4	II

Operating temperature range	-30...+55 °C

Maximum humidity	933%

Dimensions	63 x 136 x 49 mm

Weight	COBALT	136 g

COBALT PLUS	144 g

COBALT PRO	145 g

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o. • ul. Budowlanych 66 • 80-298 Gdańsk • POLAND tel. 58 320 94 00 www.satel.eu

druk (4na1):

4,1,4,1,2,3,2,3