|  | WATER FLOOD DETECTOR FD-1 |
| --- | --- |

fd1_en 01/09

The FD-1 water flood detector is designed to be used in spaces where there is a risk of leakage from water installation. Approximately 4 seconds after the water level reaches the height at which the flood sensor electrodes are installed, the detector starts signaling flooding (the relay activates). A few seconds after the water level drops below the height at which the flood sensor electrodes are installed, the signaling stops (the relay deactivates).

Explanations for Fig. 1:

1	-	terminals for connecting the flood sensor.

2	-	pins for switching the indicator LED on/off. Signaling by means of the indicator LED is on, when jumper is placed on the pins.

3	-	LED indicating the relay status. Its color is red when the relay is active.

4	-	tamper contact, which responds to opening the housing and pulling it off from the surface.

5	-	terminals:

+12V	–	power input

COM	–	common ground

TMP	–	tamper contact

NC	–	relay (NC)

The detector is monitoring power supply voltage. In case of a prolonged voltage drop below 9 V (±5%), it will signal trouble by activating the alarm relay and steady lighting of the LED indicator. Restoration of minimum 9 V (±5%) voltage will stop the trouble signaling.

The detector is suitable for use in burglary and panic alarm systems.

# Installation

The detector is designed for indoor installation.

- Select the place where the detector is to be installed.

- Open the housing.

- Make a hole for the flood sensor wires in the housing.

- Pass the flood sensor wires through the hole in the housing and screw them to the terminals on electronics board.

- Secure the rear panel of the housing to the mounting surface.

- Close the detector housing.

- Test the detector for proper operation, by submerging the flood sensor in water.

- Fasten the sensor cables and the sensor itself. The detector is ready for work.

# Technical data

Rated supply voltage	12 V DC (±15%)

Current consumption, standby	2,5 mA

Current consumption, maximum	4 mA

Probe wire length	3 m

Environmental class	II

Working temperature range	-10 °C...+55 °C

Housing dimensions	24 x 110 x 27 mm

Weight	81 g

| The latest EC declaration of conformity and product approval certificates are available for downloading on website www.satel.pl |  |
| --- | --- |

SATEL sp. z o.o.

ul. Schuberta 79

80-172 Gdańsk

POLAND

tel. + 48 58 320 94 00

info@satel.pl

www.satel.pl

druk (4 na 1)

1,2,1,2,1,2,1,2

# Text boxes

Fig. 1. View of detector electronics board.