|  | WATER FLOOD DETECTOR FD-1 |  |
| --- | --- | --- |

fd1_en 01/12

The FD-1 water flood detector is designed to be used in spaces where there is a risk of leakage from water installation. Approximately 4 seconds after the water level reaches the height at which the flood sensor electrodes are installed, the detector starts signaling flooding (relay contacts open). A few seconds after the water level drops below the height at which the flood sensor electrodes are installed, the signaling stops (relay contacts close).

Explanations for Fig. 1:

1	-	terminals for connecting the flood sensor.

2	-	pins for switching the indicator LED on/off. Signaling by means of the indicator LED is on, when jumper is placed on the pins.

3	-	LED indicating the relay status. It lights red when the relay is open.

4	-	tamper contact (NC). It opens when the cover is removed or the enclosure is torn off from the wall.

5	-	terminals:

+12V	–	power input

COM	–	common ground

TMP	–	tamper contact

NC	–	relay (NC)

The detector is monitoring power supply voltage. In case of a prolonged voltage drop below 9 V (±5%), relay contacts open. After restoration of minimum 9 V (±5%) voltage, relay contacts will close.

The detector is suitable for use in burglary and panic alarm systems.

# Installation

The detector is designed for indoor installation.

- Select the place where the detector is to be installed.

- Open the enclosure.

- Make a hole for the flood sensor wires in the enclosure.

- Pass the flood sensor wires through the hole in the enclosure and screw them to the terminals on electronics board.

- Secure the enclosure base to the mounting surface.

- Close the detector enclosure.

- Test the detector for proper operation, by submerging the flood sensor in water.

- Fasten the sensor cables and the sensor itself. The detector is ready for work.

# Specifications

Rated Supply voltage	12 V DC (±15%)

Current consumption, standby	2,5 mA

Current consumption, maximum	4 mA

Relay contacts rating (resistive load)	40 mA / 16 V DC

Probe wire length	3 m

Environmental class	II

Working temperature range	-10 °C...+55 °C

Enclosure dimensions	24 x 110 x 27 mm

Weight	81 g

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o.

ul. Schuberta 79

80-172 Gdańsk

POLAND

tel. + 48 58 320 94 00

info@satel.pl

www.satel.pl

druk (4 na 1)

1,2,1,2,1,2,1,2

# Text boxes

Fig. 1. View of detector electronics board.