GRAPHITE

DIGITAL PASSIVE INFRARED DETECTOR

graphite_en 07/11

The GRAPHITE digital motion detector is characterized by high sensitivity, as well as high immunity to interference and false alarms. The detector construction is based on an advanced signal processor with a high resolution transducer. A dual pyroelectric sensor is used in the detector. An advanced digital temperature compensation feature enables operation within a wide range of temperatures. Other advantages of the detector include alarm memory and remote on/off switching of the LED indicator.

Fig. 1. View of the detector electronics board.

Explanations for Figure 1:

1	–	terminals:

NC	–	relay (NC).

TMP	–	tamper contact.

COM	–	common ground.

12V	–	power supply input.

LED	–	the input enables the LED indicator to be remotely switched ON/OFF, if the jumper is removed from the LED ON/OFF pins. The LED will signal violations, when the LED input is short-circuited to the common ground. For control of the input, you can use the OC type output of the control panel, programmed e.g. as Service mode indicator or BI switch.

MEM	–	the alarm memory control input. It is required that the OC type output of the alarm control panel, programmed as Armed status indicator be connected to the input. When the input is shorted to the ground and the detector registers a motion, thus triggering the alarm, the LED blinking will signal the alarm memory. The alarm memory signaling will continue until the input is shorted to the ground again. Cut-off of the input from the ground (disarming) will not erase of the alarm memory.

2	–	LED indicator. It lights red for approx. 2 seconds after registration of movement by the detector and activation of the relay (opening of the NC contacts). It allows the installer to check the detector performance and to approximately determine the coverage area. Blinking of the LED indicates alarm memory.

3	–	LED ON/OFF pins. Setting the jumper will activate signaling by means of the LED, irrespective of the LED input status.

4	–	pyroelectric sensor.

5	–	tamper contact.

6	–	scale for positioning of pyroelectric sensor against the lens (see Table 1 and Figure 5).

7	–	mounting screw hole.

8	–	potentiometer for detector sensitivity adjustment.

For 30 seconds after the power-up, the detector warms up. Only after this time has elapsed, the detector will be ready to work. Warm-up is indicated by a rapid LED blinking.

The detector is monitoring power supply voltage and availability of the signal path. In case of a voltage drop below 9 V (±5%), lasting longer than 2 seconds, or detection of a fault in the signal path, the detector will signal a trouble by activating the alarm relay and steady lighting of the LED. The signaling continues as long as the trouble exists.

# Installation

- Open the enclosure as shown in Figure 2.

Fig. 2. Removing the cover.

- Remove the electronics board.

- Make suitable holes for screws and cable in the enclosure base.

- Pass the cable through the prepared opening.

- Secure the enclosure base to the attached bracket or the wall.

Note:	For compliance with the requirements of EN50131-2-2, the detector shall be installed directly on the mounting surface, without the additional bracket.

Fig. 3. Ways of installing the detector.

Fig. 4. Mounting the detector on bracket.

- Fasten the electronics board, taking into account the height at which the detector is mounted (see Table 1 and Figure 5).

| Mounting height | Scale position in relation to enclosure indicator |
| --- | --- |
| above 2.4m | middle scale mark above the index |
| 2.4m | middle scale mark aligned with the index |
| below 2.4m | middle scale mark below the index |

Table 1. Positioning the pyroelctric sensor against the lens.

Note:	If the detector is installed at a height above 2.4m, it is recommended that the bracket be used, and the detector be mounted in inclined position.

- Connect the wires to corresponding terminals.

- Using potentiometer, determine sensitivity of the detector.

- Close the detector enclosure.

Fig. 5. Effect of the height of installation on the detector coverage area and the way of positioning the electronics board to optimize the area. Depending on the mounting height, the medium scale line should be: aligned with the mark on the enclosure (installation at a height of 2.4 m), situated above the mark (installation higher than 2.4 m – example B) or below the mark (installation lower than 2.4 m – example D).

# Start-up

- Turn power supply on (the LED will start blinking, which indicates the starting state).

- When the detector is ready to work (the LED stops blinking), carry out a test for the detector range, i.e. check that a movement within the coverage area will activate the alarm relay or cause the LED light up. During the test, the LED ON/OFF pins must be shorted, or the LED input must be shorted to the common ground.

- If necessary, change the detector sensitivity.

# Specifications

Supply voltage	12 V DC 15%

Current consumption, standby	12 mA

Current consumption, maximum	14 mA

Relay contacts rated load (resistive)	40 mA / 16 V DC

Violation signaling time	2s

Detectable motion speed	0.3...3 m/s

Security grade according to EN50131-2-2	Grade 2

Environmental class according to EN50130-5	II

Operating temperature range	-30...+55°C

Standards complied with	EN50131-1, EN50131-2-2, EN50130-4, EN50130-5

Dimensions	62x96x48 mm

Recommended mounting height	2.4 m

Weight	96 g

The declaration of conformity may be consulted at www.satel.eu/ce

Fig. 6. Coverage area of a detector.

SATEL sp. z o.o.

ul. Schuberta 79

80-172 Gdańsk

POLAND

tel. + 48 58 320 94 00

info@satel.pl

www.satel.eu