INT-O

OUTPUT EXPANDER

int-o_en 06/14

The INT-O expander enables the system to be expanded by 8 programmable wired outputs. The expander works with INTEGRA, INTEGRA Plus, VERSA and CA-64 control panels.

# Features

8 programmable hardwired outputs:

8 OC type outputs,

8 relay outputs,

each OC type output connected in parallel with a relay output,

possibility to reduce current consumption by disabling support for selected relay outputs.

NC type tamper input.

Capable of being integrated with dedicated power supply unit (operation in "expander with power supply" mode).

Connectable to RS-485 bus (firmware update through the bus).

# Electronics board

Explanations to Fig. 1:

connector for a dedicated power supply unit (e.g. APS-412). If a power supply is connected to the connector, the expander will be identified as an expander with power supply.

LEDs indicating the status of the outputs:

OFF – output inactive,

ON – output active.

DIP-switches to enable / disable support for relay outputs (see: Support for relay outputs).

STS LED indicating the status of power supply connected to the connector:

ON – power supply is working normally,

blinking – power supply is reporting a trouble.

DIP-switches for setting address (see: Address setting).

LED indicating the status of communication with the control panel:

ON – no communication with the control panel,

blinking – communication with the control panel OK.

Description of terminals:

OC1...OC8	-	OC type output.

C1...C8	-	relay output common contact.

NO1...NO8	-	relay output normally open contact.

NC1...NC8	-	relay output normally closed contact.

COM	-	common ground.

TMP	-	tamper input (NC) – if not used, it should be shorted to the common ground.

CLK	-	clock (communication bus).

DAT	-	data (communication bus).

+12V	-	+12 V DC power input / output.

Do not connect power to the terminals, if the dedicated power supply unit is connected to the connector on electronics board.

A, B	-	RS-485 bus.

# Address setting

To set address, use the switches 1-5 of the DIP-switch package marked 5 in Fig. 1. A numerical value is assigned to each switch. In OFF position, the value is 0. Numerical values assigned to individual switches in ON position are shown in Table 1. The sum of numerical values assigned to switches 1-5 means the address set on the module. The address must be different from that on the other modules connected to the communication bus of the control panel. If the module is used in conjunction with the VERSA control panel, an address 15 (0Fh) must be set.

| DIP-switch number | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Numerical value | 1 | 2 | 4 | 8 | 16 |

Table 1.

Fig. 2 shows typical address settings.

# Support for relay outputs

In order to reduce current consumption by the expander, you can enable / disable support for individual relay outputs, using the DIP-switch package marked 3 in Fig. 1. The switch number corresponds to the number of onboard output. The relay output is supported when the switch is set to ON position.

Note:	Disabling the relay output support has no effect on the OC type output.

# Installation and start-up

Disconnect power before making any electrical connections.

The expander is designed for indoor installation.

- Fasten the expander electronics board in the enclosure.

- Set the expander address (see: Address setting).

- Define which relay outputs are and which are not to be supported (see: Support for relay outputs).

- Connect the CLK, DAT and COM terminals to the corresponding terminals of the control panel communication bus (see: installer manual for alarm control panel). It is recommended that an unshielded non-twisted cable be used to make the connection. If you use the twisted-pair type of cable, remember that CLK (clock) and DAT (data) signals must not be sent through one pair of twisted conductors. The conductors must be run in one cable.

- If the expander is to supervise the enclosure tamper contact, connect the wires of tamper contact to the TMP and COM terminals. If the expander is not to supervise the enclosure tamper contact, connect the TMP terminal to the expander COM terminal.

- Depending on the selected method of expander powering, connect the dedicated power supply unit to the connector on expander electronics board or connect the power leads to the +12V and COM terminals (the expander may be powered directly from the control panel, from an expander with power supply or from a power supply unit).

The expander must not be powered from both sources at the same time.

- Power on the alarm system.

- Start the identification function in the control panel. After expander identification is completed, the outputs will be assigned their respective numbers in the alarm system. The output numeration rules are described in the control panel manual. The control panel monitors presence of the identified modules. If the module is disconnected from communication bus, position of DIP-switches is changed, or the device is replaced with another one with DIP-switches set in the same way, a tamper alarm will be triggered.

- Configure the outputs and check that they operate properly (the output status is indicated by LEDs).

- Power off the alarm system.

- Connect to expander outputs the devices whose operation is to be controlled by the control panel.

- Power on the alarm system.

Notes:

If the dedicated power supply unit is connected to the connector on electronics board, the device will be identified as expander with power supply (INT-OPS or CA-64 OPS).

The expander will be identified as INT-O / INT-OPS by INTEGRA / INTEGRA Plus control panels with firmware version 1.12 or newer. Other control panels identify it as CA-64 O / CA-64 OPS.

# Updating the expander firmware

Using the RS-485 bus, connect the expander to the ACCO-USB converter, and then connect the converter to the computer (see: ACCO-USB converter manual). You can find a program for updating the expander firmware and a detailed description of the firmware update procedure on the www.satel.eu website.

# Specifications

Supply voltage	12 V DC 15%

Standby current consumption	30 mA

Maximum current consumption	160 mA

Current consumption by active relay	16 mA

OC type output rating	50 mA / 12 V DC

Relay output rating (resistive load)	2 A / 24 V DC

+12V output rating	2.5 A / 12 V DC

Security grade according to EN50131 – without power supply	Grade 3

Security grade according to EN50131 – with APS-412 power supply	Grade 2

Environmental class according to EN50130-5	II

Operating temperature range	-10 °C...+55 °C

Maximum humidity	933%

Dimensions	140 x 68 mm

Weight	90 g

The declaration of conformity may be consulted at www.satel.eu/ce

SATEL sp. z o.o. • ul. Schuberta 79 • 80-172 Gdańsk • POLAND tel. + 48 58 320 94 00 info@satel.pl www.satel.eu

druk (4 na 1):

4,1,4,1,2,3,2,3